{"text_format":"2","workbook":"xlsx","n_sheets":6,"sheets":["Version","State","Adjust","Command","Measure","causeOfTrip"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Version","index":0,"n_rows":2,"n_cols":2,"rows_kept":2,"cut":false,"hidden":false,"merged":[]}
["Handoff","SW-Version"]
[61795,"3.10.a"]

{"sheet":"State","index":1,"n_rows":1245,"n_cols":9,"rows_kept":1245,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["/SG1","Removed-I",256,1,"3","Bit","0x1","-","State of the module input: The withdrawable circuit breaker is Removed"]
["/SG1","CES SG removed",256,1,"3","Bit","0x2","-","Signal: Command Execution Supervision: Switching Command unsuccessful, Switchgear removed."]
["/SG1","Removed",256,1,"3","Bit","0x4","-","Signal: The withdrawable circuit breaker is Removed"]
["BO Slot X2","BO 1",1003,1,"3","Bit","0x1","-","Signal: Binary Output Relay"]
["BO Slot X2","BO 2",1003,1,"3","Bit","0x2","-","Signal: Binary Output Relay"]
["BO Slot X2","BO 3",1003,1,"3","Bit","0x4","-","Signal: Binary Output Relay"]
["BO Slot X2","BO 4",1003,1,"3","Bit","0x8","-","Signal: Binary Output Relay"]
["BO Slot X2","BO 5",1003,1,"3","Bit","0x10","-","Signal: Binary Output Relay"]
["BO Slot X2","BO 6",1003,1,"3","Bit","0x20","-","Signal: Binary Output Relay"]
["BO Slot X2","DISARMED!",1003,1,"3","Bit","0x40","-","Signal: CAUTION! RELAYS DISARMED in order to safely perform maintenance while eliminating the risk of taking an entire process off-line. (Note: The Self Supervision Contact cannot be disarmed). YOU MUST ENSURE that the relays are ARMED AGAIN after maintenance"]
["BO Slot X2","Outs forced",1003,1,"3","Bit","0x80","-","Signal: The State of at least one Relay Output has been set by force. That means that the state of at least one Relay is forced and hence does not show  the state of the assigned signals."]
["BO Slot X6","BO 1",1004,1,"3","Bit","0x1","-","Signal: Binary Output Relay"]
["BO Slot X6","BO 2",1004,1,"3","Bit","0x2","-","Signal: Binary Output Relay"]
["BO Slot X6","BO 3",1004,1,"3","Bit","0x4","-","Signal: Binary Output Relay"]
["BO Slot X6","BO 4",1004,1,"3","Bit","0x8","-","Signal: Binary Output Relay"]
["BO Slot X6","BO 5",1004,1,"3","Bit","0x10","-","Signal: Binary Output Relay"]
["BO Slot X6","BO 6",1004,1,"3","Bit","0x20","-","Signal: Binary Output Relay"]
["BO Slot X6","DISARMED!",1004,1,"3","Bit","0x40","-","Signal: CAUTION! RELAYS DISARMED in order to safely perform maintenance while eliminating the risk of taking an entire process off-line. (Note: The Self Supervision Contact cannot be disarmed). YOU MUST ENSURE that the relays are ARMED AGAIN after maintenance"]
["BO Slot X6","Outs forced",1004,1,"3","Bit","0x80","-","Signal: The State of at least one Relay Output has been set by force. That means that the state of at least one Relay is forced and hence does not show  the state of the assigned signals."]
["CBF","ExBlo1-I",53,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["CBF","ExBlo2-I",53,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["CBF","Active",53,1,"3","Bit","0x4","-","Signal: active"]
["CBF","ExBlo",53,1,"3","Bit","0x8","-","Signal: External Blocking"]
["CBF","Trigger1-I",53,1,"3","Bit","0x10","-","Module Input: Trigger that will start the CBF"]
["CBF","Trigger2-I",53,1,"3","Bit","0x20","-","Module Input: Trigger that will start the CBF"]
["CBF","Trigger3-I",53,1,"3","Bit","0x40","-","Module Input: Trigger that will start the CBF"]
["CBF","running",53,1,"3","Bit","0x80","-","Signal: CBF-Module started"]
["CBF","Alarm (*)",53,1,"3","Bit","0x100","-","Signal: Circuit Breaker Failure"]
["CBF","Lockout (*)",53,1,"3","Bit","0x200","-","Signal: Lockout"]
["CBF","Waiting for Trigger (*)",53,1,"3","Bit","0x400","-","Waiting for Trigger"]
["CTS","ExBlo1-I",137,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["CTS","ExBlo2-I",137,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["CTS","Active",137,1,"3","Bit","0x4","-","Signal: active"]
["CTS","ExBlo",137,1,"3","Bit","0x8","-","Signal: External Blocking"]
["CTS","Alarm",137,1,"3","Bit","0x10","-","Signal: Alarm Current Transformer Measuring Circuit Supervision"]
["Ctrl","Local",176,1,"3","Bit","0x1","-","Switching Authority: Local"]
["Ctrl","Remote",176,1,"3","Bit","0x2","-","Switching Authority: Remote"]
["Ctrl","NonInterl",176,1,"3","Bit","0x4","-","Non-Interlocking is active"]
["Ctrl","SG Disturb",176,1,"3","Bit","0x8","-","(At least one) Switchgear is disturbed."]
["Ctrl","SG Indeterm",176,1,"3","Bit","0x10","-","(At least one) Switchgear is moving (Position cannot be determined)."]
["DI Slot X1","DI 1",1000,1,"3","Bit","0x1","-","Signal: Digital Input"]
["DI Slot X1","DI 2",1000,1,"3","Bit","0x2","-","Signal: Digital Input"]
["DI Slot X1","DI 3",1000,1,"3","Bit","0x4","-","Signal: Digital Input"]
["DI Slot X1","DI 4",1000,1,"3","Bit","0x8","-","Signal: Digital Input"]
["DI Slot X1","DI 5",1000,1,"3","Bit","0x10","-","Signal: Digital Input"]
["DI Slot X1","DI 6",1000,1,"3","Bit","0x20","-","Signal: Digital Input"]
["DI Slot X1","DI 7",1000,1,"3","Bit","0x40","-","Signal: Digital Input"]
["DI Slot X1","DI 8",1000,1,"3","Bit","0x80","-","Signal: Digital Input"]
["ExP[1]","ExBlo1-I",49,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["ExP[1]","ExBlo2-I",49,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["ExP[1]","ExBlo TripCmd-I",49,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["ExP[1]","Alarm-I",49,1,"3","Bit","0x8","-","Module input state: Alarm"]
["ExP[1]","Trip-I",49,1,"3","Bit","0x10","-","Module input state: Trip"]
["ExP[1]","Active",49,1,"3","Bit","0x20","-","Signal: active"]
["ExP[1]","ExBlo",49,1,"3","Bit","0x40","-","Signal: External Blocking"]
["ExP[1]","Blo TripCmd",49,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["ExP[1]","ExBlo TripCmd",49,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["ExP[1]","Alarm",49,1,"3","Bit","0x200","-","Signal: Alarm"]
["ExP[1]","Trip (*)",49,1,"3","Bit","0x400","-","Signal: Trip"]
["ExP[1]","TripCmd (*)",49,1,"3","Bit","0x800","-","Signal: Trip Command"]
["ExP[2]","ExBlo1-I",50,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["ExP[2]","ExBlo2-I",50,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["ExP[2]","ExBlo TripCmd-I",50,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["ExP[2]","Alarm-I",50,1,"3","Bit","0x8","-","Module input state: Alarm"]
["ExP[2]","Trip-I",50,1,"3","Bit","0x10","-","Module input state: Trip"]
["ExP[2]","Active",50,1,"3","Bit","0x20","-","Signal: active"]
["ExP[2]","ExBlo",50,1,"3","Bit","0x40","-","Signal: External Blocking"]
["ExP[2]","Blo TripCmd",50,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["ExP[2]","ExBlo TripCmd",50,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["ExP[2]","Alarm",50,1,"3","Bit","0x200","-","Signal: Alarm"]
["ExP[2]","Trip (*)",50,1,"3","Bit","0x400","-","Signal: Trip"]
["ExP[2]","TripCmd (*)",50,1,"3","Bit","0x800","-","Signal: Trip Command"]
["ExP[3]","ExBlo1-I",51,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["ExP[3]","ExBlo2-I",51,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["ExP[3]","ExBlo TripCmd-I",51,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["ExP[3]","Alarm-I",51,1,"3","Bit","0x8","-","Module input state: Alarm"]
["ExP[3]","Trip-I",51,1,"3","Bit","0x10","-","Module input state: Trip"]
["ExP[3]","Active",51,1,"3","Bit","0x20","-","Signal: active"]
["ExP[3]","ExBlo",51,1,"3","Bit","0x40","-","Signal: External Blocking"]
["ExP[3]","Blo TripCmd",51,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["ExP[3]","ExBlo TripCmd",51,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["ExP[3]","Alarm",51,1,"3","Bit","0x200","-","Signal: Alarm"]
["ExP[3]","Trip (*)",51,1,"3","Bit","0x400","-","Signal: Trip"]
["ExP[3]","TripCmd (*)",51,1,"3","Bit","0x800","-","Signal: Trip Command"]
["ExP[4]","ExBlo1-I",52,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["ExP[4]","ExBlo2-I",52,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["ExP[4]","ExBlo TripCmd-I",52,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["ExP[4]","Alarm-I",52,1,"3","Bit","0x8","-","Module input state: Alarm"]
["ExP[4]","Trip-I",52,1,"3","Bit","0x10","-","Module input state: Trip"]
["ExP[4]","Active",52,1,"3","Bit","0x20","-","Signal: active"]
["ExP[4]","ExBlo",52,1,"3","Bit","0x40","-","Signal: External Blocking"]
["ExP[4]","Blo TripCmd",52,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["ExP[4]","ExBlo TripCmd",52,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["ExP[4]","Alarm",52,1,"3","Bit","0x200","-","Signal: Alarm"]
["ExP[4]","Trip (*)",52,1,"3","Bit","0x400","-","Signal: Trip"]
["ExP[4]","TripCmd (*)",52,1,"3","Bit","0x800","-","Signal: Trip Command"]
["Fast Status Register","Device Type",5000,1,"3","Bit","0xffff","-","Device type code for relationship between device name and its Modbus code. \\nHighPROTEC: \\nMRI4 - 1000\\nMRU4 - 1001\\nMRA4 - 1002\\nMCA4 - 1003\\nMRDT4 - 1005\\nMCDTV4 - 1006\\nMCDGV4 - 1007\\nMRM4 - 1009\\nMRMV4 - 1010\\nMCDLV4 - 1011"]
["Fast Status Register","Comm Version",5001,1,"3","Bit","0xffff","-","Modbus Communication version. This version number changes if something becomes incompatible between different Modbus releases."]
["Fast Status Register","Config Bin Inp1-I",5002,1,"3","Bit","0x1","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp2-I",5002,1,"3","Bit","0x2","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp3-I",5002,1,"3","Bit","0x4","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp4-I",5002,1,"3","Bit","0x8","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp5-I",5002,1,"3","Bit","0x10","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp6-I",5002,1,"3","Bit","0x20","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp7-I",5002,1,"3","Bit","0x40","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp8-I",5002,1,"3","Bit","0x80","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp9-I",5002,1,"3","Bit","0x100","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp10-I",5002,1,"3","Bit","0x200","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp11-I",5002,1,"3","Bit","0x400","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp12-I",5002,1,"3","Bit","0x800","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp13-I",5002,1,"3","Bit","0x1000","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp14-I",5002,1,"3","Bit","0x2000","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp15-I",5002,1,"3","Bit","0x4000","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp16-I",5002,1,"3","Bit","0x8000","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp17-I",5003,1,"3","Bit","0x1","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp18-I",5003,1,"3","Bit","0x2","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp19-I",5003,1,"3","Bit","0x4","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp20-I",5003,1,"3","Bit","0x8","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp21-I",5003,1,"3","Bit","0x10","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp22-I",5003,1,"3","Bit","0x20","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp23-I",5003,1,"3","Bit","0x40","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp24-I",5003,1,"3","Bit","0x80","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp25-I",5003,1,"3","Bit","0x100","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp26-I",5003,1,"3","Bit","0x200","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp27-I",5003,1,"3","Bit","0x400","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp28-I",5003,1,"3","Bit","0x800","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp29-I",5003,1,"3","Bit","0x1000","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp30-I",5003,1,"3","Bit","0x2000","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp31-I",5003,1,"3","Bit","0x4000","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Config Bin Inp32-I",5003,1,"3","Bit","0x8000","-","State of the module input: Config Bin Inp"]
["Fast Status Register","Trip Cause (*)",5004,1,"3","Bit","0xffff","-","Initial reason of trip. It is presented as an integer value and corresponds to the “Trip” entry in the fault record, which refers to the name of the protective module that tripped first. Look up the definition of these integer values (i. e. the mapping trip code number-->module name) in the “Cause of Trip” table within the SCADA documentation."]
["I2>[1]","ExBlo1-I",82,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I2>[1]","ExBlo2-I",82,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I2>[1]","ExBlo TripCmd-I",82,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I2>[1]","Active",82,1,"3","Bit","0x8","-","Signal: active"]
["I2>[1]","ExBlo",82,1,"3","Bit","0x10","-","Signal: External Blocking"]
["I2>[1]","Blo TripCmd",82,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["I2>[1]","ExBlo TripCmd",82,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["I2>[1]","Alarm",82,1,"3","Bit","0x80","-","Signal: Alarm Negative Sequence"]
["I2>[1]","Trip (*)",82,1,"3","Bit","0x100","-","Signal: Trip"]
["I2>[1]","TripCmd (*)",82,1,"3","Bit","0x200","-","Signal: Trip Command"]
["I2>[2]","ExBlo1-I",83,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I2>[2]","ExBlo2-I",83,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I2>[2]","ExBlo TripCmd-I",83,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I2>[2]","Active",83,1,"3","Bit","0x8","-","Signal: active"]
["I2>[2]","ExBlo",83,1,"3","Bit","0x10","-","Signal: External Blocking"]
["I2>[2]","Blo TripCmd",83,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["I2>[2]","ExBlo TripCmd",83,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["I2>[2]","Alarm",83,1,"3","Bit","0x80","-","Signal: Alarm Negative Sequence"]
["I2>[2]","Trip (*)",83,1,"3","Bit","0x100","-","Signal: Trip"]
["I2>[2]","TripCmd (*)",83,1,"3","Bit","0x200","-","Signal: Trip Command"]
["I<[1]","ExBlo1-I",167,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I<[1]","ExBlo2-I",167,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I<[1]","ExBlo TripCmd-I",167,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I<[1]","Active",167,1,"3","Bit","0x10","-","Signal: active"]
["I<[1]","ExBlo",167,1,"3","Bit","0x20","-","Signal: External Blocking"]
["I<[1]","Blo TripCmd",167,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["I<[1]","ExBlo TripCmd",167,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["I<[1]","Alarm",167,1,"3","Bit","0x200","-","Signal: Alarm"]
["I<[1]","Trip (*)",167,1,"3","Bit","0x400","-","Signal: Trip"]
["I<[1]","TripCmd (*)",167,1,"3","Bit","0x800","-","Signal: Trip Command"]
["I<[2]","ExBlo1-I",168,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I<[2]","ExBlo2-I",168,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I<[2]","ExBlo TripCmd-I",168,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I<[2]","Active",168,1,"3","Bit","0x10","-","Signal: active"]
["I<[2]","ExBlo",168,1,"3","Bit","0x20","-","Signal: External Blocking"]
["I<[2]","Blo TripCmd",168,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["I<[2]","ExBlo TripCmd",168,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["I<[2]","Alarm",168,1,"3","Bit","0x200","-","Signal: Alarm"]
["I<[2]","Trip (*)",168,1,"3","Bit","0x400","-","Signal: Trip"]
["I<[2]","TripCmd (*)",168,1,"3","Bit","0x800","-","Signal: Trip Command"]
["I<[3]","ExBlo1-I",169,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I<[3]","ExBlo2-I",169,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I<[3]","ExBlo TripCmd-I",169,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I<[3]","Active",169,1,"3","Bit","0x10","-","Signal: active"]
["I<[3]","ExBlo",169,1,"3","Bit","0x20","-","Signal: External Blocking"]
["I<[3]","Blo TripCmd",169,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["I<[3]","ExBlo TripCmd",169,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["I<[3]","Alarm",169,1,"3","Bit","0x200","-","Signal: Alarm"]
["I<[3]","Trip (*)",169,1,"3","Bit","0x400","-","Signal: Trip"]
["I<[3]","TripCmd (*)",169,1,"3","Bit","0x800","-","Signal: Trip Command"]
["IG[1]","ExBlo1-I",15,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["IG[1]","ExBlo2-I",15,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["IG[1]","ExBlo TripCmd-I",15,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["IG[1]","Ex rev Interl-I",15,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["IG[1]","Active",15,1,"3","Bit","0x10","-","Signal: active"]
["IG[1]","ExBlo",15,1,"3","Bit","0x20","-","Signal: External Blocking"]
["IG[1]","Ex rev Interl",15,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["IG[1]","Blo TripCmd",15,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["IG[1]","ExBlo TripCmd",15,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["IG[1]","Alarm",15,1,"3","Bit","0x400","-","Signal: The alarm threshold has been exceeded."]
["IG[1]","Trip (*)",15,1,"3","Bit","0x800","-","Signal: Trip"]
["IG[1]","TripCmd (*)",15,1,"3","Bit","0x1000","-","Signal: Trip Command"]
["IG[2]","ExBlo1-I",16,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["IG[2]","ExBlo2-I",16,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["IG[2]","ExBlo TripCmd-I",16,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["IG[2]","Ex rev Interl-I",16,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["IG[2]","Active",16,1,"3","Bit","0x10","-","Signal: active"]
["IG[2]","ExBlo",16,1,"3","Bit","0x20","-","Signal: External Blocking"]
["IG[2]","Ex rev Interl",16,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["IG[2]","Blo TripCmd",16,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["IG[2]","ExBlo TripCmd",16,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["IG[2]","Alarm",16,1,"3","Bit","0x400","-","Signal: The alarm threshold has been exceeded."]
["IG[2]","Trip (*)",16,1,"3","Bit","0x800","-","Signal: Trip"]
["IG[2]","TripCmd (*)",16,1,"3","Bit","0x1000","-","Signal: Trip Command"]
["IG[3]","ExBlo1-I",17,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["IG[3]","ExBlo2-I",17,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["IG[3]","ExBlo TripCmd-I",17,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["IG[3]","Ex rev Interl-I",17,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["IG[3]","Active",17,1,"3","Bit","0x10","-","Signal: active"]
["IG[3]","ExBlo",17,1,"3","Bit","0x20","-","Signal: External Blocking"]
["IG[3]","Ex rev Interl",17,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["IG[3]","Blo TripCmd",17,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["IG[3]","ExBlo TripCmd",17,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["IG[3]","Alarm",17,1,"3","Bit","0x400","-","Signal: The alarm threshold has been exceeded."]
["IG[3]","Trip (*)",17,1,"3","Bit","0x800","-","Signal: Trip"]
["IG[3]","TripCmd (*)",17,1,"3","Bit","0x1000","-","Signal: Trip Command"]
["IG[4]","ExBlo1-I",18,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["IG[4]","ExBlo2-I",18,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["IG[4]","ExBlo TripCmd-I",18,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["IG[4]","Ex rev Interl-I",18,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["IG[4]","Active",18,1,"3","Bit","0x10","-","Signal: active"]
["IG[4]","ExBlo",18,1,"3","Bit","0x20","-","Signal: External Blocking"]
["IG[4]","Ex rev Interl",18,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["IG[4]","Blo TripCmd",18,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["IG[4]","ExBlo TripCmd",18,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["IG[4]","Alarm",18,1,"3","Bit","0x400","-","Signal: The alarm threshold has been exceeded."]
["IG[4]","Trip (*)",18,1,"3","Bit","0x800","-","Signal: Trip"]
["IG[4]","TripCmd (*)",18,1,"3","Bit","0x1000","-","Signal: Trip Command"]
["IRIG-B","IRIG-B active",148,1,"3","Bit","0x1","-","Signal: If there is no valid IRIG-B signal for 60 sec, IRIG-B is regarded as inactive."]
["IRIG-B","High-Low Invert",148,1,"3","Bit","0x2","-","Signal: The High and Low signals of the IRIG-B are inverted. This does NOT mean that the wiring is faulty. If the wiring is faulty no IRIG-B signal will be detected."]
["I[1]","ExBlo1-I",3,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I[1]","ExBlo2-I",3,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I[1]","ExBlo TripCmd-I",3,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I[1]","Ex rev Interl-I",3,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["I[1]","Active",3,1,"3","Bit","0x10","-","Signal: active"]
["I[1]","ExBlo",3,1,"3","Bit","0x20","-","Signal: External Blocking"]
["I[1]","Ex rev Interl",3,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["I[1]","Blo TripCmd",3,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["I[1]","ExBlo TripCmd",3,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["I[1]","Alarm L1",4,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["I[1]","Alarm L2",4,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["I[1]","Alarm L3",4,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["I[1]","Alarm",4,1,"3","Bit","0x8","-","Signal: Alarm"]
["I[1]","Trip L1 (*)",4,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["I[1]","Trip L2 (*)",4,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["I[1]","Trip L3 (*)",4,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["I[1]","Trip (*)",4,1,"3","Bit","0x80","-","Signal: Trip"]
["I[1]","TripCmd (*)",4,1,"3","Bit","0x100","-","Signal: Trip Command"]
["I[2]","ExBlo1-I",5,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I[2]","ExBlo2-I",5,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I[2]","ExBlo TripCmd-I",5,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I[2]","Ex rev Interl-I",5,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["I[2]","Active",5,1,"3","Bit","0x10","-","Signal: active"]
["I[2]","ExBlo",5,1,"3","Bit","0x20","-","Signal: External Blocking"]
["I[2]","Ex rev Interl",5,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["I[2]","Blo TripCmd",5,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["I[2]","ExBlo TripCmd",5,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["I[2]","Alarm L1",6,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["I[2]","Alarm L2",6,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["I[2]","Alarm L3",6,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["I[2]","Alarm",6,1,"3","Bit","0x8","-","Signal: Alarm"]
["I[2]","Trip L1 (*)",6,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["I[2]","Trip L2 (*)",6,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["I[2]","Trip L3 (*)",6,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["I[2]","Trip (*)",6,1,"3","Bit","0x80","-","Signal: Trip"]
["I[2]","TripCmd (*)",6,1,"3","Bit","0x100","-","Signal: Trip Command"]
["I[3]","ExBlo1-I",7,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I[3]","ExBlo2-I",7,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I[3]","ExBlo TripCmd-I",7,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I[3]","Ex rev Interl-I",7,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["I[3]","Active",7,1,"3","Bit","0x10","-","Signal: active"]
["I[3]","ExBlo",7,1,"3","Bit","0x20","-","Signal: External Blocking"]
["I[3]","Ex rev Interl",7,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["I[3]","Blo TripCmd",7,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["I[3]","ExBlo TripCmd",7,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["I[3]","Alarm L1",8,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["I[3]","Alarm L2",8,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["I[3]","Alarm L3",8,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["I[3]","Alarm",8,1,"3","Bit","0x8","-","Signal: Alarm"]
["I[3]","Trip L1 (*)",8,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["I[3]","Trip L2 (*)",8,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["I[3]","Trip L3 (*)",8,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["I[3]","Trip (*)",8,1,"3","Bit","0x80","-","Signal: Trip"]
["I[3]","TripCmd (*)",8,1,"3","Bit","0x100","-","Signal: Trip Command"]
["I[4]","ExBlo1-I",9,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I[4]","ExBlo2-I",9,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I[4]","ExBlo TripCmd-I",9,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I[4]","Ex rev Interl-I",9,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["I[4]","Active",9,1,"3","Bit","0x10","-","Signal: active"]
["I[4]","ExBlo",9,1,"3","Bit","0x20","-","Signal: External Blocking"]
["I[4]","Ex rev Interl",9,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["I[4]","Blo TripCmd",9,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["I[4]","ExBlo TripCmd",9,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["I[4]","Alarm L1",10,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["I[4]","Alarm L2",10,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["I[4]","Alarm L3",10,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["I[4]","Alarm",10,1,"3","Bit","0x8","-","Signal: Alarm"]
["I[4]","Trip L1 (*)",10,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["I[4]","Trip L2 (*)",10,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["I[4]","Trip L3 (*)",10,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["I[4]","Trip (*)",10,1,"3","Bit","0x80","-","Signal: Trip"]
["I[4]","TripCmd (*)",10,1,"3","Bit","0x100","-","Signal: Trip Command"]
["I[5]","ExBlo1-I",11,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I[5]","ExBlo2-I",11,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I[5]","ExBlo TripCmd-I",11,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I[5]","Ex rev Interl-I",11,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["I[5]","Active",11,1,"3","Bit","0x10","-","Signal: active"]
["I[5]","ExBlo",11,1,"3","Bit","0x20","-","Signal: External Blocking"]
["I[5]","Ex rev Interl",11,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["I[5]","Blo TripCmd",11,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["I[5]","ExBlo TripCmd",11,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["I[5]","Alarm L1",12,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["I[5]","Alarm L2",12,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["I[5]","Alarm L3",12,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["I[5]","Alarm",12,1,"3","Bit","0x8","-","Signal: Alarm"]
["I[5]","Trip L1 (*)",12,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["I[5]","Trip L2 (*)",12,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["I[5]","Trip L3 (*)",12,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["I[5]","Trip (*)",12,1,"3","Bit","0x80","-","Signal: Trip"]
["I[5]","TripCmd (*)",12,1,"3","Bit","0x100","-","Signal: Trip Command"]
["I[6]","ExBlo1-I",13,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["I[6]","ExBlo2-I",13,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["I[6]","ExBlo TripCmd-I",13,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["I[6]","Ex rev Interl-I",13,1,"3","Bit","0x8","-","Module input state: External reverse interlocking"]
["I[6]","Active",13,1,"3","Bit","0x10","-","Signal: active"]
["I[6]","ExBlo",13,1,"3","Bit","0x20","-","Signal: External Blocking"]
["I[6]","Ex rev Interl",13,1,"3","Bit","0x40","-","Signal: External reverse Interlocking"]
["I[6]","Blo TripCmd",13,1,"3","Bit","0x80","-","Signal: Trip Command blocked"]
["I[6]","ExBlo TripCmd",13,1,"3","Bit","0x100","-","Signal: External Blocking of the Trip Command"]
["I[6]","Alarm L1",14,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["I[6]","Alarm L2",14,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["I[6]","Alarm L3",14,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["I[6]","Alarm",14,1,"3","Bit","0x8","-","Signal: Alarm"]
["I[6]","Trip L1 (*)",14,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["I[6]","Trip L2 (*)",14,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["I[6]","Trip L3 (*)",14,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["I[6]","Trip (*)",14,1,"3","Bit","0x80","-","Signal: Trip"]
["I[6]","TripCmd (*)",14,1,"3","Bit","0x100","-","Signal: Trip Command"]
["Jam[1]","ExBlo1-I",165,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["Jam[1]","ExBlo2-I",165,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["Jam[1]","ExBlo TripCmd-I",165,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["Jam[1]","Active",165,1,"3","Bit","0x10","-","Signal: active"]
["Jam[1]","ExBlo",165,1,"3","Bit","0x20","-","Signal: External Blocking"]
["Jam[1]","Blo TripCmd",165,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["Jam[1]","ExBlo TripCmd",165,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["Jam[1]","Alarm",165,1,"3","Bit","0x200","-","Signal: Alarm"]
["Jam[1]","Trip (*)",165,1,"3","Bit","0x400","-","Signal: Trip"]
["Jam[1]","TripCmd (*)",165,1,"3","Bit","0x800","-","Signal: Trip Command"]
["Jam[2]","ExBlo1-I",166,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["Jam[2]","ExBlo2-I",166,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["Jam[2]","ExBlo TripCmd-I",166,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["Jam[2]","Active",166,1,"3","Bit","0x10","-","Signal: active"]
["Jam[2]","ExBlo",166,1,"3","Bit","0x20","-","Signal: External Blocking"]
["Jam[2]","Blo TripCmd",166,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["Jam[2]","ExBlo TripCmd",166,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["Jam[2]","Alarm",166,1,"3","Bit","0x200","-","Signal: Alarm"]
["Jam[2]","Trip (*)",166,1,"3","Bit","0x400","-","Signal: Trip"]
["Jam[2]","TripCmd (*)",166,1,"3","Bit","0x800","-","Signal: Trip Command"]
["LOP","ExBlo1-I",81,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["LOP","ExBlo2-I",81,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["LOP","Active",81,1,"3","Bit","0x4","-","Signal: active"]
["LOP","ExBlo",81,1,"3","Bit","0x8","-","Signal: External Blocking"]
["LOP","LOP Blo",81,1,"3","Bit","0x10","-","Signal: Loss of Potential blocks other elements."]
["LOP","Alarm",81,1,"3","Bit","0x20","-","Signal: Alarm Loss of Potential"]
["LOP","Ex FF EVT",81,1,"3","Bit","0x1000","-","Signal:  Alarm Fuse Failure Earth Voltage Transformers"]
["LOP","Ex FF VT",81,1,"3","Bit","0x2000","-","Signal: Ex FF VT"]
["LOP","Ex FF EVT-I",202,1,"3","Bit","0x1","-","State of the module input:  Alarm Fuse Failure Earth Voltage Transformers"]
["LOP","Ex FF VT-I",202,1,"3","Bit","0x2","-","State of the module input:  Alarm Fuse Failure Voltage Transformers"]
["LOP","Blo Trigger1-I",202,1,"3","Bit","0x4","-","State of the module input: An Alarm of this protective element will block the Loss of Potential Detection."]
["LOP","Blo Trigger2-I",202,1,"3","Bit","0x8","-","State of the module input: An Alarm of this protective element will block the Loss of Potential Detection."]
["LOP","Blo Trigger3-I",202,1,"3","Bit","0x10","-","State of the module input: An Alarm of this protective element will block the Loss of Potential Detection."]
["LOP","Blo Trigger4-I",202,1,"3","Bit","0x20","-","State of the module input: An Alarm of this protective element will block the Loss of Potential Detection."]
["LOP","Blo Trigger5-I",202,1,"3","Bit","0x40","-","State of the module input: An Alarm of this protective element will block the Loss of Potential Detection."]
["Logics","LE1.Gate Out",1100,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE1.Timer Out",1100,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE1.Out",1100,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE1.Out inverted",1100,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE1.Gate In1-I",1100,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE1.Gate In2-I",1100,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE1.Gate In3-I",1100,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE1.Gate In4-I",1100,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE1.Reset Latch-I",1100,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE2.Gate Out",1101,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE2.Timer Out",1101,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE2.Out",1101,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE2.Out inverted",1101,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE2.Gate In1-I",1101,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE2.Gate In2-I",1101,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE2.Gate In3-I",1101,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE2.Gate In4-I",1101,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE2.Reset Latch-I",1101,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE3.Gate Out",1102,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE3.Timer Out",1102,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE3.Out",1102,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE3.Out inverted",1102,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE3.Gate In1-I",1102,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE3.Gate In2-I",1102,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE3.Gate In3-I",1102,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE3.Gate In4-I",1102,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE3.Reset Latch-I",1102,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE4.Gate Out",1103,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE4.Timer Out",1103,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE4.Out",1103,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE4.Out inverted",1103,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE4.Gate In1-I",1103,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE4.Gate In2-I",1103,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE4.Gate In3-I",1103,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE4.Gate In4-I",1103,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE4.Reset Latch-I",1103,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE5.Gate Out",1104,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE5.Timer Out",1104,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE5.Out",1104,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE5.Out inverted",1104,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE5.Gate In1-I",1104,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE5.Gate In2-I",1104,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE5.Gate In3-I",1104,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE5.Gate In4-I",1104,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE5.Reset Latch-I",1104,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE6.Gate Out",1105,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE6.Timer Out",1105,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE6.Out",1105,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE6.Out inverted",1105,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE6.Gate In1-I",1105,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE6.Gate In2-I",1105,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE6.Gate In3-I",1105,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE6.Gate In4-I",1105,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE6.Reset Latch-I",1105,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE7.Gate Out",1106,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE7.Timer Out",1106,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE7.Out",1106,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE7.Out inverted",1106,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE7.Gate In1-I",1106,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE7.Gate In2-I",1106,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE7.Gate In3-I",1106,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE7.Gate In4-I",1106,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE7.Reset Latch-I",1106,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE8.Gate Out",1107,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE8.Timer Out",1107,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE8.Out",1107,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE8.Out inverted",1107,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE8.Gate In1-I",1107,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE8.Gate In2-I",1107,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE8.Gate In3-I",1107,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE8.Gate In4-I",1107,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE8.Reset Latch-I",1107,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE9.Gate Out",1108,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE9.Timer Out",1108,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE9.Out",1108,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE9.Out inverted",1108,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE9.Gate In1-I",1108,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE9.Gate In2-I",1108,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE9.Gate In3-I",1108,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE9.Gate In4-I",1108,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE9.Reset Latch-I",1108,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE10.Gate Out",1109,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE10.Timer Out",1109,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE10.Out",1109,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE10.Out inverted",1109,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE10.Gate In1-I",1109,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE10.Gate In2-I",1109,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE10.Gate In3-I",1109,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE10.Gate In4-I",1109,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE10.Reset Latch-I",1109,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE11.Gate Out",1110,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE11.Timer Out",1110,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE11.Out",1110,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE11.Out inverted",1110,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE11.Gate In1-I",1110,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE11.Gate In2-I",1110,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE11.Gate In3-I",1110,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE11.Gate In4-I",1110,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE11.Reset Latch-I",1110,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE12.Gate Out",1111,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE12.Timer Out",1111,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE12.Out",1111,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE12.Out inverted",1111,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE12.Gate In1-I",1111,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE12.Gate In2-I",1111,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE12.Gate In3-I",1111,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE12.Gate In4-I",1111,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE12.Reset Latch-I",1111,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE13.Gate Out",1112,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE13.Timer Out",1112,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE13.Out",1112,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE13.Out inverted",1112,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE13.Gate In1-I",1112,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE13.Gate In2-I",1112,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE13.Gate In3-I",1112,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE13.Gate In4-I",1112,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE13.Reset Latch-I",1112,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE14.Gate Out",1113,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE14.Timer Out",1113,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE14.Out",1113,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE14.Out inverted",1113,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE14.Gate In1-I",1113,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE14.Gate In2-I",1113,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE14.Gate In3-I",1113,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE14.Gate In4-I",1113,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE14.Reset Latch-I",1113,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE15.Gate Out",1114,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE15.Timer Out",1114,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE15.Out",1114,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE15.Out inverted",1114,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE15.Gate In1-I",1114,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE15.Gate In2-I",1114,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE15.Gate In3-I",1114,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE15.Gate In4-I",1114,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE15.Reset Latch-I",1114,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE16.Gate Out",1115,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE16.Timer Out",1115,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE16.Out",1115,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE16.Out inverted",1115,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE16.Gate In1-I",1115,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE16.Gate In2-I",1115,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE16.Gate In3-I",1115,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE16.Gate In4-I",1115,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE16.Reset Latch-I",1115,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE17.Gate Out",1116,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE17.Timer Out",1116,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE17.Out",1116,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE17.Out inverted",1116,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE17.Gate In1-I",1116,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE17.Gate In2-I",1116,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE17.Gate In3-I",1116,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE17.Gate In4-I",1116,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE17.Reset Latch-I",1116,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE18.Gate Out",1117,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE18.Timer Out",1117,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE18.Out",1117,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE18.Out inverted",1117,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE18.Gate In1-I",1117,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE18.Gate In2-I",1117,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE18.Gate In3-I",1117,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE18.Gate In4-I",1117,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE18.Reset Latch-I",1117,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE19.Gate Out",1118,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE19.Timer Out",1118,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE19.Out",1118,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE19.Out inverted",1118,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE19.Gate In1-I",1118,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE19.Gate In2-I",1118,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE19.Gate In3-I",1118,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE19.Gate In4-I",1118,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE19.Reset Latch-I",1118,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["Logics","LE20.Gate Out",1119,1,"3","Bit","0x1","-","Signal: Output of the logic gate"]
["Logics","LE20.Timer Out",1119,1,"3","Bit","0x2","-","Signal: Timer Output"]
["Logics","LE20.Out",1119,1,"3","Bit","0x4","-","Signal: Latched Output (Q)"]
["Logics","LE20.Out inverted",1119,1,"3","Bit","0x8","-","Signal: Negated Latched Output (Q NOT)"]
["Logics","LE20.Gate In1-I",1119,1,"3","Bit","0x10","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE20.Gate In2-I",1119,1,"3","Bit","0x20","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE20.Gate In3-I",1119,1,"3","Bit","0x40","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE20.Gate In4-I",1119,1,"3","Bit","0x80","-","State of the module input: Assignment of the Input Signal"]
["Logics","LE20.Reset Latch-I",1119,1,"3","Bit","0x100","-","State of the module input: Reset Signal for the Latching"]
["MLS","ExBlo1-I",170,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["MLS","ExBlo2-I",170,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["MLS","Active",170,1,"3","Bit","0x4","-","Signal: active"]
["MLS","ExBlo",170,1,"3","Bit","0x8","-","Signal: External Blocking"]
["MLS","Alarm",170,1,"3","Bit","0x10","-","Signal: Alarm"]
["MLS","Trip",170,1,"3","Bit","0x20","-","Signal: Trip"]
["MStart","ExBlo TripCmd-I",160,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["MStart","Blo TripCmd",160,1,"3","Bit","0x10","-","Signal: Trip Command blocked"]
["MStart","Blo",160,1,"3","Bit","0x40","-","Signal: Motor is blocked for starting or transition to Run mode"]
["MStart","ThermalBlo",160,1,"3","Bit","0x80","-","Signal: Thermal block"]
["MStart","EmgOvr-I",160,1,"3","Bit","0x100","-","State of the module input: Emergency Override. Signal has to be active in order to release the thermal capacity of the motor. Please notice that by doing this you run the risk of damaging the motor. “EMGOVR” has to be set to “DI” or “DI or UI” for this input to take effect"]
["MStart","InSq-I",160,1,"3","Bit","0x200","-","State of the module input: Incomplete Sequence"]
["MStart","RemStartBlock-I",161,1,"3","Bit","0x2","-","State of the module input: Remote Motor Start Blocking"]
["MStart","ZSS-I",161,1,"3","Bit","0x10","-","State of the module input: Zero Speed Switch"]
["MStart","Active",161,1,"3","Bit","0x80","-","Signal: active"]
["MStart","Trip (*)",161,1,"3","Bit","0x400","-","Signal: Trip"]
["MStart","TripCmd (*)",161,1,"3","Bit","0x800","-","Signal: Trip Command"]
["MStart","InSq Start2Run Fail",161,1,"3","Bit","0x1000","-","Signal: Fail to transit from start to run based on reported back time"]
["MStart","InSq Stop2Start Faill",161,1,"3","Bit","0x2000","-","Signal: Fail to transit from stop to start based on reported back time"]
["MStart","LATBlock",161,1,"3","Bit","0x4000","-","Signal: Long acceleration timer enforced"]
["MStart","TripPhaseReverse (*)",161,1,"3","Bit","0x8000","-","Signal: Relay tripped because of phase reverse detection"]
["MStart","NOCSBlocked",162,1,"3","Bit","0x1","-","Signal: Motor is prohibited to start due to number of cold start limits"]
["MStart","RemBlockStart",162,1,"3","Bit","0x2","-","Signal: Motor is prohibited to start due to external blocking through digital input DI"]
["MStart","Run",162,1,"3","Bit","0x4","-","Signal: Motor is in run mode"]
["MStart","Start",162,1,"3","Bit","0x8","-","Signal: Motor is in start mode"]
["MStart","SPHBlockAlarm",162,1,"3","Bit","0x10","-","Signal: Motor is prohibited to start due to starts per hour limits, would come active in the next stop"]
["MStart","SPHBlocked",162,1,"3","Bit","0x20","-","Signal: Motor is prohibited to start due to starts per hour limits"]
["MStart","Stop",162,1,"3","Bit","0x40","-","Signal: Motor is in stop mode"]
["MStart","TBSBlocked",162,1,"3","Bit","0x80","-","Signal: Motor is prohibited to start due to time between starts limits"]
["MStart","TransitionTrip (*)",162,1,"3","Bit","0x100","-","Signal: Start transition fail trip"]
["MStart","ZSSTrip (*)",162,1,"3","Bit","0x200","-","Signal: Zero speed trip (possible locked rotor)"]
["MStart","ABSActive",162,1,"3","Bit","0x400","-","Signal: Anti-backspin is active. For certain applications, such as pumping a fluid up a pipe, the motor may be driven backward for a period of time after it stops. The anti-backspin timer prevents starting the motor while it is spinning in the reverse direction."]
["MStart","EmergOverrideDI",162,1,"3","Bit","0x800","-","Signal: Emergency override start blocking through digital input DI"]
["MStart","EmergOverrideUI",162,1,"3","Bit","0x1000","-","Signal: Emergency override start blocking through front panel"]
["MStart","ForcedStart",162,1,"3","Bit","0x2000","-","Signal: Motor being forced to start"]
["MStart","Blo-GOCStart",162,1,"3","Bit","0x4000","-","Signal: Ground Instantaneous Overcurrent Start Delay. GOC (Instantaneous Overcurrent) elements are blocked for the time programmed under this parameter"]
["MStart","Blo-IOCStart",162,1,"3","Bit","0x8000","-","Signal: Phase Instantaneous Overcurrent Start Delay. IOC (Instantaneous Overcurrent) elements are blocked for the time programmed under this parameter"]
["MStart","Blo-JamStart",163,1,"3","Bit","0x1","-","Signal: JAM Start Delay. JAM(Instantaneous Overcurrent) elements are blocked for the time programmed under this parameter"]
["MStart","Blo-I<Start",163,1,"3","Bit","0x2","-","Signal: Underload Start Delay. Underload(Instantaneous Overcurrent) elements are blocked for the time programmed under this parameter"]
["MStart","Blo-I2>Start",163,1,"3","Bit","0x4","-","Signal: Motor start block current unbalance signal"]
["MStart","ColdStartSeq",163,1,"3","Bit","0x8","-","Signal: Motor cold start sequence flag"]
["MStart","MotorStopBlo",163,1,"3","Bit","0x20","-","Signal: Motor stop block other protection functions"]
["MStart","Blo-Generic1",163,1,"3","Bit","0x40","-","Generic Start Delay. This value can be used to block any protective element.1"]
["MStart","Blo-Generic2",163,1,"3","Bit","0x80","-","Generic Start Delay. This value can be used to block any protective element.2"]
["MStart","Blo-Generic3",163,1,"3","Bit","0x100","-","Generic Start Delay. This value can be used to block any protective element.3"]
["MStart","Blo-Generic4",163,1,"3","Bit","0x200","-","Generic Start Delay. This value can be used to block any protective element.4"]
["MStart","Blo-Generic5",163,1,"3","Bit","0x400","-","Generic Start Delay. This value can be used to block any protective element.5"]
["MStart","I_Transit",163,1,"3","Bit","0x800","-","Signal: Current transition signal"]
["MStart","T_Transit",163,1,"3","Bit","0x1000","-","Signal: Time transition signal"]
["MStart","Rotating forward",163,1,"3","Bit","0x2000","-","Signal: Rotation Direction forward"]
["MStart","Rotating backward",163,1,"3","Bit","0x4000","-","Signal: Rotation Direction reverse"]
["MStart","STPC Blo-I",163,1,"3","Bit","0x8000","-","State of the module input: With this setting a Digital Input keeps the Motor in the RUN mode, even when the motor current drops below STPC (motor stop current). "]
["MStart","Blo-FrqStart",204,1,"3","Bit","0x1","-","Signal: Frequency Start Delay. Frequency elements are blocked for the time programmed under this parameter"]
["MStart","Block-OverVStart",204,1,"3","Bit","0x2","-","Signal: Overvoltage Start Delay. Overvoltage elements are blocked for the time programmed under this parameter"]
["MStart","Blo-PFacStart",204,1,"3","Bit","0x4","-","Signal: Power Factor Start Delay. Power Factor elements are blocked for the time programmed under this parameter"]
["MStart","Blo-PowerStart",204,1,"3","Bit","0x8","-","Signal: Power Start Delay. Power elements are blocked for the time programmed under this parameter"]
["MStart","Blo-UnderV Start",204,1,"3","Bit","0x10","-","Signal: Undervoltage Start Delay. Undervoltage elements are blocked for the time programmed under this parameter"]
["MStart","Blo-U2>",204,1,"3","Bit","0x20","-","Signal: Motor start block voltage unbalance signal."]
["Modbus","Scada Cmd 1",1005,1,"3","Bit","0x1","-","Scada Command"]
["Modbus","Scada Cmd 2",1005,1,"3","Bit","0x2","-","Scada Command"]
["Modbus","Scada Cmd 3",1005,1,"3","Bit","0x4","-","Scada Command"]
["Modbus","Scada Cmd 4",1005,1,"3","Bit","0x8","-","Scada Command"]
["Modbus","Scada Cmd 5",1005,1,"3","Bit","0x10","-","Scada Command"]
["Modbus","Scada Cmd 6",1005,1,"3","Bit","0x20","-","Scada Command"]
["Modbus","Scada Cmd 7",1005,1,"3","Bit","0x40","-","Scada Command"]
["Modbus","Scada Cmd 8",1005,1,"3","Bit","0x80","-","Scada Command"]
["Modbus","Scada Cmd 9",1005,1,"3","Bit","0x100","-","Scada Command"]
["Modbus","Scada Cmd 10",1005,1,"3","Bit","0x200","-","Scada Command"]
["Modbus","Scada Cmd 11",1005,1,"3","Bit","0x400","-","Scada Command"]
["Modbus","Scada Cmd 12",1005,1,"3","Bit","0x800","-","Scada Command"]
["Modbus","Scada Cmd 13",1005,1,"3","Bit","0x1000","-","Scada Command"]
["Modbus","Scada Cmd 14",1005,1,"3","Bit","0x2000","-","Scada Command"]
["Modbus","Scada Cmd 15",1005,1,"3","Bit","0x4000","-","Scada Command"]
["Modbus","Scada Cmd 16",1005,1,"3","Bit","0x8000","-","Scada Command"]
["PF[1]","ExBlo1-I",73,1,"3","Bit","0x1","-","Module input state: External blocking"]
["PF[1]","ExBlo2-I",73,1,"3","Bit","0x2","-","Module input state: External blocking"]
["PF[1]","ExBlo TripCmd-I",73,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["PF[1]","Active",73,1,"3","Bit","0x8","-","Signal: active"]
["PF[1]","ExBlo",73,1,"3","Bit","0x10","-","Signal: External Blocking"]
["PF[1]","Blo TripCmd",73,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["PF[1]","ExBlo TripCmd",73,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["PF[1]","Alarm",73,1,"3","Bit","0x80","-","Signal: Alarm Power Factor"]
["PF[1]","Trip (*)",73,1,"3","Bit","0x100","-","Signal: Trip Power Factor"]
["PF[1]","TripCmd (*)",73,1,"3","Bit","0x200","-","Signal: Trip Command"]
["PF[1]","Compensator",73,1,"3","Bit","0x400","-","Signal: Compensation Signal"]
["PF[1]","Impossible",73,1,"3","Bit","0x800","-","Signal: Alarm Power Factor Impossible"]
["PF[2]","ExBlo1-I",74,1,"3","Bit","0x1","-","Module input state: External blocking"]
["PF[2]","ExBlo2-I",74,1,"3","Bit","0x2","-","Module input state: External blocking"]
["PF[2]","ExBlo TripCmd-I",74,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["PF[2]","Active",74,1,"3","Bit","0x8","-","Signal: active"]
["PF[2]","ExBlo",74,1,"3","Bit","0x10","-","Signal: External Blocking"]
["PF[2]","Blo TripCmd",74,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["PF[2]","ExBlo TripCmd",74,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["PF[2]","Alarm",74,1,"3","Bit","0x80","-","Signal: Alarm Power Factor"]
["PF[2]","Trip (*)",74,1,"3","Bit","0x100","-","Signal: Trip Power Factor"]
["PF[2]","TripCmd (*)",74,1,"3","Bit","0x200","-","Signal: Trip Command"]
["PF[2]","Compensator",74,1,"3","Bit","0x400","-","Signal: Compensation Signal"]
["PF[2]","Impossible",74,1,"3","Bit","0x800","-","Signal: Alarm Power Factor Impossible"]
["PQSCr","Cr Oflw Wp+",60,1,"3","Bit","0x1","-","Signal: Counter Overflow Wp+"]
["PQSCr","Cr Oflw Wp-",60,1,"3","Bit","0x2","-","Signal: Counter Overflow Wp-"]
["PQSCr","Cr Oflw Wq+",60,1,"3","Bit","0x4","-","Signal: Counter Overflow Wq+"]
["PQSCr","Cr Oflw Wq-",60,1,"3","Bit","0x8","-","Signal: Counter Overflow Wq-"]
["PQSCr","Cr Oflw Wp Net",60,1,"3","Bit","0x10","-","Signal: Counter Overflow Wp Net"]
["PQSCr","Cr Oflw Wq Net",60,1,"3","Bit","0x20","-","Signal: Counter Overflow Wq Net"]
["PQSCr","Cr Oflw Ws Net",60,1,"3","Bit","0x40","-","Signal: Counter Overflow Ws Net"]
["PQSCr","Cr OflwW Wp+",60,1,"3","Bit","0x80","-","Signal: Counter Wp+ will overflow soon"]
["PQSCr","Cr OflwW Wp-",60,1,"3","Bit","0x100","-","Signal: Counter Wp- will overflow soon"]
["PQSCr","Cr OflwW Wq+",60,1,"3","Bit","0x200","-","Signal: Counter Wq+ will overflow soon"]
["PQSCr","Cr OflwW Wq-",60,1,"3","Bit","0x400","-","Signal: Counter Wq- will overflow soon"]
["PQSCr","Cr OflwW Wp Net",60,1,"3","Bit","0x800","-","Signal: Counter Wp Net will overflow soon"]
["PQSCr","Cr OflwW Wq Net",60,1,"3","Bit","0x1000","-","Signal: Counter Wq Net will overflow soon"]
["PQSCr","Cr OflwW Ws Net",60,1,"3","Bit","0x2000","-","Signal: Counter Ws Net will overflow soon"]
["PQS[1]","ExBlo1-I",67,1,"3","Bit","0x1","-","Module input state: External blocking"]
["PQS[1]","ExBlo2-I",67,1,"3","Bit","0x2","-","Module input state: External blocking"]
["PQS[1]","ExBlo TripCmd-I",67,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["PQS[1]","Active",67,1,"3","Bit","0x8","-","Signal: active"]
["PQS[1]","ExBlo",67,1,"3","Bit","0x10","-","Signal: External Blocking"]
["PQS[1]","Blo TripCmd",67,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["PQS[1]","ExBlo TripCmd",67,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["PQS[1]","Alarm",67,1,"3","Bit","0x80","-","Signal: Alarm Power Protection"]
["PQS[1]","Trip (*)",67,1,"3","Bit","0x100","-","Signal: Trip Power Protection"]
["PQS[1]","TripCmd (*)",67,1,"3","Bit","0x200","-","Signal: Trip Command"]
["PQS[2]","ExBlo1-I",68,1,"3","Bit","0x1","-","Module input state: External blocking"]
["PQS[2]","ExBlo2-I",68,1,"3","Bit","0x2","-","Module input state: External blocking"]
["PQS[2]","ExBlo TripCmd-I",68,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["PQS[2]","Active",68,1,"3","Bit","0x8","-","Signal: active"]
["PQS[2]","ExBlo",68,1,"3","Bit","0x10","-","Signal: External Blocking"]
["PQS[2]","Blo TripCmd",68,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["PQS[2]","ExBlo TripCmd",68,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["PQS[2]","Alarm",68,1,"3","Bit","0x80","-","Signal: Alarm Power Protection"]
["PQS[2]","Trip (*)",68,1,"3","Bit","0x100","-","Signal: Trip Power Protection"]
["PQS[2]","TripCmd (*)",68,1,"3","Bit","0x200","-","Signal: Trip Command"]
["PQS[3]","ExBlo1-I",69,1,"3","Bit","0x1","-","Module input state: External blocking"]
["PQS[3]","ExBlo2-I",69,1,"3","Bit","0x2","-","Module input state: External blocking"]
["PQS[3]","ExBlo TripCmd-I",69,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["PQS[3]","Active",69,1,"3","Bit","0x8","-","Signal: active"]
["PQS[3]","ExBlo",69,1,"3","Bit","0x10","-","Signal: External Blocking"]
["PQS[3]","Blo TripCmd",69,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["PQS[3]","ExBlo TripCmd",69,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["PQS[3]","Alarm",69,1,"3","Bit","0x80","-","Signal: Alarm Power Protection"]
["PQS[3]","Trip (*)",69,1,"3","Bit","0x100","-","Signal: Trip Power Protection"]
["PQS[3]","TripCmd (*)",69,1,"3","Bit","0x200","-","Signal: Trip Command"]
["PQS[4]","ExBlo1-I",70,1,"3","Bit","0x1","-","Module input state: External blocking"]
["PQS[4]","ExBlo2-I",70,1,"3","Bit","0x2","-","Module input state: External blocking"]
["PQS[4]","ExBlo TripCmd-I",70,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["PQS[4]","Active",70,1,"3","Bit","0x8","-","Signal: active"]
["PQS[4]","ExBlo",70,1,"3","Bit","0x10","-","Signal: External Blocking"]
["PQS[4]","Blo TripCmd",70,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["PQS[4]","ExBlo TripCmd",70,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["PQS[4]","Alarm",70,1,"3","Bit","0x80","-","Signal: Alarm Power Protection"]
["PQS[4]","Trip (*)",70,1,"3","Bit","0x100","-","Signal: Trip Power Protection"]
["PQS[4]","TripCmd (*)",70,1,"3","Bit","0x200","-","Signal: Trip Command"]
["PQS[5]","ExBlo1-I",71,1,"3","Bit","0x1","-","Module input state: External blocking"]
["PQS[5]","ExBlo2-I",71,1,"3","Bit","0x2","-","Module input state: External blocking"]
["PQS[5]","ExBlo TripCmd-I",71,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["PQS[5]","Active",71,1,"3","Bit","0x8","-","Signal: active"]
["PQS[5]","ExBlo",71,1,"3","Bit","0x10","-","Signal: External Blocking"]
["PQS[5]","Blo TripCmd",71,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["PQS[5]","ExBlo TripCmd",71,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["PQS[5]","Alarm",71,1,"3","Bit","0x80","-","Signal: Alarm Power Protection"]
["PQS[5]","Trip (*)",71,1,"3","Bit","0x100","-","Signal: Trip Power Protection"]
["PQS[5]","TripCmd (*)",71,1,"3","Bit","0x200","-","Signal: Trip Command"]
["PQS[6]","ExBlo1-I",72,1,"3","Bit","0x1","-","Module input state: External blocking"]
["PQS[6]","ExBlo2-I",72,1,"3","Bit","0x2","-","Module input state: External blocking"]
["PQS[6]","ExBlo TripCmd-I",72,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["PQS[6]","Active",72,1,"3","Bit","0x8","-","Signal: active"]
["PQS[6]","ExBlo",72,1,"3","Bit","0x10","-","Signal: External Blocking"]
["PQS[6]","Blo TripCmd",72,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["PQS[6]","ExBlo TripCmd",72,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["PQS[6]","Alarm",72,1,"3","Bit","0x80","-","Signal: Alarm Power Protection"]
["PQS[6]","Trip (*)",72,1,"3","Bit","0x100","-","Signal: Trip Power Protection"]
["PQS[6]","TripCmd (*)",72,1,"3","Bit","0x200","-","Signal: Trip Command"]
["PSet-Switch","PS 1",59,1,"3","Bit","0x1","-","Signal: The currently active Parameter Set is PS 1"]
["PSet-Switch","PS 2",59,1,"3","Bit","0x2","-","Signal: The currently active Parameter Set is PS 2"]
["PSet-Switch","PS 3",59,1,"3","Bit","0x4","-","Signal: The currently active Parameter Set is PS 3"]
["PSet-Switch","PS 4",59,1,"3","Bit","0x8","-","Signal: The currently active Parameter Set is PS 4"]
["PSet-Switch","PSS manual",59,1,"3","Bit","0x10","-","Signal: Manual Switch over of a Parameter Set"]
["PSet-Switch","PSS via Scada",59,1,"3","Bit","0x20","-","Signal: Parameter Set Switch via Scada. Write into this output byte the integer of the parameter set that should become active (e.g.  4 => Switch onto parameter set 4)."]
["PSet-Switch","PSS via Inp fct",59,1,"3","Bit","0x40","-","Signal: Parameter Set Switch via input function"]
["PSet-Switch","PS1-I",59,1,"3","Bit","0x80","-","State of the module input respectively of the signal, that should activate this Parameter Setting Group."]
["PSet-Switch","PS2-I",59,1,"3","Bit","0x100","-","State of the module input respectively of the signal, that should activate this Parameter Setting Group."]
["PSet-Switch","PS3-I",59,1,"3","Bit","0x200","-","State of the module input respectively of the signal, that should activate this Parameter Setting Group."]
["PSet-Switch","PS4-I",59,1,"3","Bit","0x400","-","State of the module input respectively of the signal, that should activate this Parameter Setting Group."]
["PSet-Switch","min 1 param changed (*)",59,1,"3","Bit","0x800","-","Signal: At least one parameter has been changed"]
["Prot","ExBlo1-I",1,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["Prot","ExBlo2-I",1,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["Prot","Active",1,1,"3","Bit","0x4","-","Signal: active"]
["Prot","ExBlo",1,1,"3","Bit","0x8","-","Signal: External Blocking"]
["Prot","Alarm L1",1,1,"3","Bit","0x10","-","Signal: General-Alarm L1"]
["Prot","Alarm L2",1,1,"3","Bit","0x20","-","Signal: General-Alarm L2"]
["Prot","Alarm L3",1,1,"3","Bit","0x40","-","Signal: General-Alarm L3"]
["Prot","Alarm G",1,1,"3","Bit","0x80","-","Signal: General-Alarm - Earth fault"]
["Prot","Alarm",1,1,"3","Bit","0x100","-","Signal: General Alarm"]
["Prot","Trip L1 (*)",1,1,"3","Bit","0x200","-","Signal: General Trip L1"]
["Prot","Trip L2 (*)",1,1,"3","Bit","0x400","-","Signal: General Trip L2"]
["Prot","Trip L3 (*)",1,1,"3","Bit","0x800","-","Signal: General Trip L3"]
["Prot","Trip G (*)",1,1,"3","Bit","0x1000","-","Signal: General Trip Ground fault"]
["Prot","Trip (*)",1,1,"3","Bit","0x2000","-","Signal: General Trip"]
["Prot","Blo TripCmd",2,1,"3","Bit","0x1","-","Signal: Trip Command blocked"]
["Prot","ExBlo TripCmd-I",2,1,"3","Bit","0x2","-","Module input state: External Blocking of the Trip Command"]
["Prot","ExBlo TripCmd",2,1,"3","Bit","0x4","-","Signal: External Blocking of the Trip Command"]
["Prot","Fault No.",57,1,"3","Bit","0xffff","-","Fault number"]
["RTD","ExBlo1-I",143,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["RTD","ExBlo2-I",143,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["RTD","ExBlo TripCmd-I",143,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["RTD","Active",143,1,"3","Bit","0x8","-","Signal: active"]
["RTD","ExBlo",143,1,"3","Bit","0x10","-","Signal: External Blocking"]
["RTD","Blo TripCmd",143,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["RTD","ExBlo TripCmd",143,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["RTD","Alarm",143,1,"3","Bit","0x80","-","Alarm RTD Temperature Protection"]
["RTD","Trip (*)",143,1,"3","Bit","0x100","-","Signal: Trip"]
["RTD","TripCmd (*)",143,1,"3","Bit","0x200","-","Signal: Trip Command"]
["RTD","Windg 1 Alarm",144,1,"3","Bit","0x1","-","Winding 1 Alarm RTD Temperature Protection"]
["RTD","Windg 1 Timeout Alarm",144,1,"3","Bit","0x2","-","Winding 1 Timeout Alarm"]
["RTD","Windg 1 Trip (*)",144,1,"3","Bit","0x4","-","Winding 1 Signal: Trip"]
["RTD","Windg 1 Invalid",144,1,"3","Bit","0x8","-","Winding 1 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Windg 2 Alarm",144,1,"3","Bit","0x10","-","Winding 2 Alarm RTD Temperature Protection"]
["RTD","Windg 2 Timeout Alarm",144,1,"3","Bit","0x20","-","Winding 2 Timeout Alarm"]
["RTD","Windg 2 Trip (*)",144,1,"3","Bit","0x40","-","Winding 2 Signal: Trip"]
["RTD","Windg 2 Invalid",144,1,"3","Bit","0x80","-","Winding 2 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Windg 3 Alarm",144,1,"3","Bit","0x100","-","Winding 3 Alarm RTD Temperature Protection"]
["RTD","Windg 3 Timeout Alarm",144,1,"3","Bit","0x200","-","Winding 3 Timeout Alarm"]
["RTD","Windg 3 Trip (*)",144,1,"3","Bit","0x400","-","Winding 3 Signal: Trip"]
["RTD","Windg 3 Invalid",144,1,"3","Bit","0x800","-","Winding 3 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Windg 4 Alarm",144,1,"3","Bit","0x1000","-","Winding 4 Alarm RTD Temperature Protection"]
["RTD","Windg 4 Timeout Alarm",144,1,"3","Bit","0x2000","-","Winding 4 Timeout Alarm"]
["RTD","Windg 4 Trip (*)",144,1,"3","Bit","0x4000","-","Winding 4 Signal: Trip"]
["RTD","Windg 4 Invalid",144,1,"3","Bit","0x8000","-","Winding 4 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Windg 5 Alarm",145,1,"3","Bit","0x1","-","Winding 5 Alarm RTD Temperature Protection"]
["RTD","Windg 5 Timeout Alarm",145,1,"3","Bit","0x2","-","Winding 5 Timeout Alarm"]
["RTD","Windg 5 Trip (*)",145,1,"3","Bit","0x4","-","Winding 5 Signal: Trip"]
["RTD","Windg 5 Invalid",145,1,"3","Bit","0x8","-","Winding 5 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Windg 6 Alarm",145,1,"3","Bit","0x10","-","Winding 6 Alarm RTD Temperature Protection"]
["RTD","Windg 6 Timeout Alarm",145,1,"3","Bit","0x20","-","Winding 6 Timeout Alarm"]
["RTD","Windg 6 Trip (*)",145,1,"3","Bit","0x40","-","Winding 6 Signal: Trip"]
["RTD","Windg 6 Invalid",145,1,"3","Bit","0x80","-","Winding 6 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","MotBear 1 Alarm",145,1,"3","Bit","0x100","-","Motor Bearing 1 Alarm RTD Temperature Protection"]
["RTD","MotBear 1 Timeout Alarm",145,1,"3","Bit","0x200","-","Motor Bearing 1 Timeout Alarm"]
["RTD","MotBear 1 Trip (*)",145,1,"3","Bit","0x400","-","Motor Bearing 1 Signal: Trip"]
["RTD","MotBear 1 Invalid",145,1,"3","Bit","0x800","-","Motor Bearing 1 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","MotBear 2 Alarm",145,1,"3","Bit","0x1000","-","Motor Bearing 2 Alarm RTD Temperature Protection"]
["RTD","MotBear 2 Timeout Alarm",145,1,"3","Bit","0x2000","-","Motor Bearing 2 Timeout Alarm"]
["RTD","MotBear 2 Trip (*)",145,1,"3","Bit","0x4000","-","Motor Bearing 2 Signal: Trip"]
["RTD","MotBear 2 Invalid",145,1,"3","Bit","0x8000","-","Motor Bearing 2 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","LoadBear 1 Alarm",146,1,"3","Bit","0x1","-","Load Bearing 1 Alarm RTD Temperature Protection"]
["RTD","LoadBear 1 Timeout Alarm",146,1,"3","Bit","0x2","-","Load Bearing 1 Timeout Alarm"]
["RTD","LoadBear 1 Trip (*)",146,1,"3","Bit","0x4","-","Load Bearing 1 Signal: Trip"]
["RTD","LoadBear 1 Invalid",146,1,"3","Bit","0x8","-","Load Bearing 1 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","LoadBear 2 Alarm",146,1,"3","Bit","0x10","-","Load Bearing 2 Alarm RTD Temperature Protection"]
["RTD","LoadBear 2 Timeout Alarm",146,1,"3","Bit","0x20","-","Load Bearing 2 Timeout Alarm"]
["RTD","LoadBear 2 Trip (*)",146,1,"3","Bit","0x40","-","Load Bearing 2 Signal: Trip"]
["RTD","LoadBear 2 Invalid",146,1,"3","Bit","0x80","-","Load Bearing 2 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Aux1 Alarm",146,1,"3","Bit","0x100","-","Auxiliary 1 Alarm RTD Temperature Protection"]
["RTD","Aux1 Timeout Alarm",146,1,"3","Bit","0x200","-","Auxiliary 1 Timeout Alarm"]
["RTD","Aux1 Trip (*)",146,1,"3","Bit","0x400","-","Auxiliary 1 Signal: Trip"]
["RTD","Aux1 Invalid",146,1,"3","Bit","0x800","-","Auxiliary 1 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Windg Group Invalid",146,1,"3","Bit","0x1000","-","Winding Group Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","MotBear Group Invalid",146,1,"3","Bit","0x2000","-","Motor Bearing Group Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Timeout Alarm (*)",146,1,"3","Bit","0x4000","-","Alarm timeout expired"]
["RTD","LoadBear Group Invalid",147,1,"3","Bit","0x1","-","Load Bearing Group Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Alarm LB Group",147,1,"3","Bit","0x2","-","Alarm all Load Bearings"]
["RTD","TimeoutAlmLBGrp",147,1,"3","Bit","0x4","-","Timeout Alarm all Load Bearings"]
["RTD","Trip LB Group (*)",147,1,"3","Bit","0x8","-","Trip all Load Bearings"]
["RTD","Alarm MB Group",147,1,"3","Bit","0x10","-","Alarm all Motor Bearings"]
["RTD","TimeoutAlmMBGrp",147,1,"3","Bit","0x20","-","Timeout Alarm all Motor Bearings"]
["RTD","Trip MB Group (*)",147,1,"3","Bit","0x40","-","Trip all Motor Bearings"]
["RTD","Alarm WD Group",147,1,"3","Bit","0x80","-","Alarm all Windings"]
["RTD","TimeoutAlmWDGrp",147,1,"3","Bit","0x100","-","Timeout Alarm all Windings"]
["RTD","Trip WD Group (*)",147,1,"3","Bit","0x200","-","Trip all Windings"]
["RTD","Trip Group 1 (*)",147,1,"3","Bit","0x2000","-","Trip Group 1"]
["RTD","Trip Group 2 (*)",147,1,"3","Bit","0x4000","-","Trip Group 2"]
["RTD","Alarm Any Group",205,1,"3","Bit","0x1","-","Alarm Any Group"]
["RTD","Trip Any Group (*)",205,1,"3","Bit","0x2","-","Trip Any Group"]
["RTD","TimeoutAlmAnyGrp",205,1,"3","Bit","0x4","-","Timeout Alarm Any Group"]
["RTD","Aux2 Alarm",205,1,"3","Bit","0x8","-","Auxiliary 2 Alarm RTD Temperature Protection"]
["RTD","Aux2 Timeout Alarm",205,1,"3","Bit","0x10","-","Auxiliary 2 Timeout Alarm"]
["RTD","Aux2 Invalid",205,1,"3","Bit","0x20","-","Auxiliary 2 Signal: Invalid Temperature Measurement Value (e.g caused by an defective or interrupted RTD Measurement)"]
["RTD","Aux2 Trip (*)",205,1,"3","Bit","0x40","-","Auxiliary 2 Signal: Trip"]
["RTD","AuxGrpInvalid",205,1,"3","Bit","0x80","-","Invalid Auxiliary Group"]
["RTD","Alarm Aux Group",205,1,"3","Bit","0x100","-","Alarm Auxiliary Group"]
["RTD","TimeoutAlmAuxGrp",205,1,"3","Bit","0x200","-","Timeout Alarm Auxiliary Group"]
["RTD","Trip Aux Group (*)",205,1,"3","Bit","0x400","-","Trip Auxiliary Group"]
["SG[1]","Isum Intr trip",123,1,"3","Bit","0x10","-","Signal: Maximum permissible Summation of the interrupting (tripping) currents exceeded in at least one phase."]
["SG[1]","Isum Intr trip:  IL1",123,1,"3","Bit","0x20","-","Signal: Maximum permissible Summation of the interrupting (tripping) currents exceeded:  IL1"]
["SG[1]","Isum Intr trip:  IL2",123,1,"3","Bit","0x40","-","Signal: Maximum permissible Summation of the interrupting (tripping) currents exceeded:  IL2"]
["SG[1]","Isum Intr trip:  IL3",123,1,"3","Bit","0x80","-","Signal: Maximum permissible Summation of the interrupting (tripping) currents exceeded:  IL3"]
["SG[1]","Operations Alarm",123,1,"3","Bit","0x100","-","Signal: Too many Operations. (The operations counter »TripCmd Cr« has exceeded the limit set at »Operations Alarm«.)"]
["SG[1]","WearLevel Alarm",123,1,"3","Bit","0x200","-","Signal: Threshold for the Alarm"]
["SG[1]","WearLevel Lockout",123,1,"3","Bit","0x400","-","Signal: Threshold for the Lockout Level"]
["SG[1]","Isum Intr ph Alm",123,1,"3","Bit","0x800","-","Signal: Alarm, the per hour Sum (Limit) of interrupting currents has been exceeded."]
["SG[1]","Aux OFF-I",177,1,"3","Bit","0x1","-","Module input state: Position indicator/check-back signal of the CB (52b)"]
["SG[1]","Aux ON-I",177,1,"3","Bit","0x2","-","Module Input State: Position indicator/check-back signal of the CB (52a)"]
["SG[1]","Ready-I",177,1,"3","Bit","0x4","-","Module input state: CB ready"]
["SG[1]","Interl OFF1-I",177,1,"3","Bit","0x10","-","State of the module input: Interlocking of the  OFF command"]
["SG[1]","Interl OFF2-I",177,1,"3","Bit","0x20","-","State of the module input: Interlocking of the  OFF command"]
["SG[1]","Interl OFF3-I",177,1,"3","Bit","0x40","-","State of the module input: Interlocking of the  OFF command"]
["SG[1]","Interl ON1-I",177,1,"3","Bit","0x80","-","State of the module input: Interlocking of the ON command"]
["SG[1]","Interl ON2-I",177,1,"3","Bit","0x100","-","State of the module input: Interlocking of the ON command"]
["SG[1]","Interl ON3-I",177,1,"3","Bit","0x200","-","State of the module input: Interlocking of the ON command"]
["SG[1]","SCmd OFF-I",177,1,"3","Bit","0x800","-","State of the module input: Switching OFF Command, e.g. the state of the Logics or the state of the digital input"]
["SG[1]","SCmd ON-I",177,1,"3","Bit","0x1000","-","State of the module input: Switching ON Command, e.g. the state of the Logics or the state of the digital input"]
["SG[1]","TripCmd (*)",177,1,"3","Bit","0x2000","-","Signal: Trip Command"]
["SG[1]","OFF Cmd",177,1,"3","Bit","0x4000","-","Signal: OFF Command issued to the switchgear. Depending on the setting the signal may include the OFF command of the Prot module."]
["SG[1]","OFF Cmd manual",177,1,"3","Bit","0x8000","-","Signal: OFF Cmd manual"]
["SG[1]","ON Cmd",178,1,"3","Bit","0x1","-","Signal: ON Command issued to the switchgear. Depending on the setting the signal may include the ON command of the Prot module."]
["SG[1]","ON Cmd manual",178,1,"3","Bit","0x2","-","Signal: ON Cmd manual"]
["SG[1]","SGwear Slow SG",178,1,"3","Bit","0x8","-","Signal: Alarm, the circuit breaker (load-break switch) becomes slower"]
["SG[1]","Res SGwear Sl SG",178,1,"3","Bit","0x10","-","Signal: Resetting the slow Switchgear Alarm"]
["SG[1]","CES Disturbed",178,1,"3","Bit","0x40","-","Signal: Command Execution Supervision: Switching Command unsuccessful. Switchgear in disturbed position."]
["SG[1]","CES Fiel Interl",178,1,"3","Bit","0x80","-","Signal: Command Execution Supervision: Switching Command not executed because of field interlocking."]
["SG[1]","CES ON d OFF",178,1,"3","Bit","0x400","-","Signal: Command Execution Supervision: On Command during a pending OFF Command."]
["SG[1]","CES SwitchDir",178,1,"3","Bit","0x800","-","Signal: Command Execution Supervision respectively Switching Direction Control: This signal becomes true, if a switch command is issued even though the switchgear is already in the requested position. Example:  A switchgear that is already OFF should be switched OFF again (doubly).  The same applies to CLOSE commands."]
["SG[1]","CES SG not ready",178,1,"3","Bit","0x1000","-","Signal: Command Execution Supervision: Switchgear not ready"]
["SG[1]","CES succesf",178,1,"3","Bit","0x4000","-","Signal: Command Execution Supervision: Switching command executed successfully."]
["SG[1]","Pos Disturb",179,1,"3","Bit","0x1","-","Signal: Circuit Breaker Disturbed - Undefined Breaker Position. The Position Indicators contradict themselves. After expiring of a supervision timer this signal becomes true."]
["SG[1]","t-Dwell",179,1,"3","Bit","0x2","-","Signal: Dwell time"]
["SG[1]","Pos Indeterm",179,1,"3","Bit","0x4","-","Signal: Circuit Breaker is in Indeterminate Position"]
["SG[1]","Pos OFF",179,1,"3","Bit","0x8","-","Signal: Circuit Breaker is in OFF-Position"]
["SG[1]","Pos ON",179,1,"3","Bit","0x10","-","Signal: Circuit Breaker is in ON-Position"]
["SG[1]","Ready",179,1,"3","Bit","0x20","-","Signal: Circuit breaker is ready for operation."]
["SG[1]","Pos not ON",179,1,"3","Bit","0x40","-","Signal: Pos not ON"]
["SG[1]","SI SingleContactInd",179,1,"3","Bit","0x80","-","Signal: The Position of the Switchgear is detected by one auxiliary contact (pole) only. Thus indeterminate and disturbed Positions cannot be detected."]
["SG[1]","Position Ind manipul",179,1,"3","Bit","0x100","-","Signal: Position Indicators faked"]
["SG[1]","OFF incl TripCmd",179,1,"3","Bit","0x200","-","Signal: The OFF Command includes the OFF Command issued by the Protection module."]
["SG[1]","CES Fail TripCmd",179,1,"3","Bit","0x800","-","Signal: Command Execution Supervision: Command execution failed because trip command is pending."]
["SG[1]","Interl OFF",179,1,"3","Bit","0x1000","-","Signal: One or more IL_Off inputs are active."]
["SG[1]","Interl ON",179,1,"3","Bit","0x2000","-","Signal: One or more IL_On inputs are active."]
["SSV","System Error",273,1,"3","Bit","0x1","-","Signal: Device Failure"]
["SSV","New error (*)",273,1,"3","Bit","0x8","-","Signal: A new error message has been issued."]
["SSV","New warning (*)",273,1,"3","Bit","0x10","-","Signal: A new warning message has been issued."]
["SSV","Active",273,1,"3","Bit","0x20","-","Signal: active"]
["Sgen","ExBlo1-I",1012,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["Sgen","Ex ForcePost-I",1012,1,"3","Bit","0x2","-","State of the module input:Force Post state. Abort simulation."]
["Sgen","Running",1012,1,"3","Bit","0x10","-","Signal: Measuring value simulation is running"]
["Sgen","State",1012,1,"3","Bit","0xe0","-","Signal: Wave generation states: 0=Off, 1=PreFault, 2=Fault, 3=PostFault, 4=InitReset"]
["Sgen","Ex Start Simulation-I",1012,1,"3","Bit","0x100","-","State of the module input:External Start of Fault Simulation (Using the test parameters)"]
["Sgen","ExBlo2-I",1012,1,"3","Bit","0x200","-","Module input state: External blocking2"]
["Sgen","Manual Start",1012,1,"3","Bit","0x400","-","Fault Simulation has been started manually."]
["Sgen","Manual Stop",1012,1,"3","Bit","0x800","-","Fault Simulation has been stopped manually."]
["Sgen","Started",1012,1,"3","Bit","0x1000","-","Fault Simulation has been started"]
["Sgen","Stopped",1012,1,"3","Bit","0x2000","-","Fault Simulation has been stopped"]
["Sys","Maint Mode Active",154,1,"3","Bit","0x1","-","Signal: Arc Flash Reduction Maintenance Active"]
["Sys","MaintMode Manually",154,1,"3","Bit","0x2","-","Signal: Arc Flash Reduction Maintenance Manual Mode"]
["Sys","Maint Mode DI",154,1,"3","Bit","0x4","-","Signal: Arc Flash Reduction Maintenance Digital Input Mode"]
["Sys","Maint Mode SCADA",154,1,"3","Bit","0x8","-","Signal: Arc Flash Reduction Maintenance SCADA Mode"]
["Sys","Maint Mode Inactive",154,1,"3","Bit","0x10","-","Signal: Arc Flash Reduction Maintenance Inactive"]
["Sys","Maint Mode-I",154,1,"3","Bit","0x20","-","Module Input State: Arc Flash Reduction Maintenance Switch"]
["Sys","SNTP active",154,1,"3","Bit","0x80","-","Signal: If there is no valid SNTP signal for 120 sec, SNTP is regarded as inactive."]
["Sys","Setting Lock Bypass",154,1,"3","Bit","0x100","-","Signal: Short-period unlock of the Setting Lock"]
["SysA","ExBlo-I",173,1,"3","Bit","0x1","-","Module input state: External blocking"]
["SysA","ExBlo",173,1,"3","Bit","0x2","-","Signal: External Blocking"]
["SysA","Alm Current avg (Demd)",173,1,"3","Bit","0x4","-","Signal: Alarm: Averaged demand current exceeded"]
["SysA","Active",173,1,"3","Bit","0x8","-","Signal: active"]
["SysA","Alarm I THD",173,1,"3","Bit","0x10","-","Signal: Alarm Total Harmonic Distortion Current"]
["SysA","Alarm VA Power max",173,1,"3","Bit","0x20","-","Signal: Alarm: Permitted Apparent Power exceeded"]
["SysA","Alarm VA avg (Demand)",173,1,"3","Bit","0x40","-","Signal: Alarm: Averaged Apparent Power exceeded"]
["SysA","Alarm VAr Power max",173,1,"3","Bit","0x80","-","Signal: Alarm: Permitted Reactive Power exceeded"]
["SysA","Alarm VAr avg (Demand)",173,1,"3","Bit","0x100","-","Signal: Alarm: Averaged Reactive Power exceeded"]
["SysA","Alarm V THD",173,1,"3","Bit","0x200","-","Signal: Alarm Total Harmonic Distortion Voltage"]
["SysA","Alarm Watt Power max",173,1,"3","Bit","0x400","-","Signal: Alarm: Permitted Active Power exceeded"]
["SysA","Alarm Watt avg (Demand)",173,1,"3","Bit","0x800","-","Signal: Alarm: Averaged Active Power exceeded"]
["SysA","Trip Current avg (Demd) (*)",173,1,"3","Bit","0x1000","-","Signal: Trip: Averaged demand current exceeded"]
["SysA","Trip I THD (*)",173,1,"3","Bit","0x2000","-","Signal: Trip Total Harmonic Distortion Current"]
["SysA","Trip VA avg (Demand) (*)",173,1,"3","Bit","0x4000","-","Signal: Trip: Averaged Apparent Power exceeded"]
["SysA","Trip VA Power max (*)",173,1,"3","Bit","0x8000","-","Signal: Trip maximum permitted Apparent Power exceeded"]
["SysA","Trip VAr avg (Demand) (*)",174,1,"3","Bit","0x1","-","Signal: Trip: Averaged Reactive Power exceeded"]
["SysA","Trip VAr Power max (*)",174,1,"3","Bit","0x2","-","Signal: Trip maximum permitted Reactive Power exceeded"]
["SysA","Trip V THD (*)",174,1,"3","Bit","0x4","-","Signal: Trip Total Harmonic Distortion Voltage"]
["SysA","Trip Watt avg (Demand) (*)",174,1,"3","Bit","0x8","-","Signal: Trip: Averaged Active Power exceeded"]
["SysA","Trip Watt Power max  (*)",174,1,"3","Bit","0x10","-","Signal: Trip maximum permitted Active Power exceeded"]
["TCS","ExBlo1-I",150,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["TCS","ExBlo2-I",150,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["TCS","Active",150,1,"3","Bit","0x4","-","Signal: active"]
["TCS","ExBlo",150,1,"3","Bit","0x8","-","Signal: External Blocking"]
["TCS","Alarm",150,1,"3","Bit","0x10","-","Signal: Alarm Trip Circuit Supervision"]
["TCS","Not Possible",150,1,"3","Bit","0x20","-","Not possible because no state indicator assigned to the breaker."]
["TCS","Aux ON-I",150,1,"3","Bit","0x100","-","Module Input State: Position indicator/check-back signal of the CB (52a)"]
["TCS","Aux OFF-I",150,1,"3","Bit","0x200","-","Module input state: Position indicator/check-back signal of the CB (52b)"]
["ThR","ExBlo1-I",164,1,"3","Bit","0x1","-","Module input state: External blocking"]
["ThR","ExBlo2-I",164,1,"3","Bit","0x2","-","Module input state: External blocking"]
["ThR","ExBlo TripCmd-I",164,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["ThR","Active",164,1,"3","Bit","0x8","-","Signal: active"]
["ThR","ExBlo",164,1,"3","Bit","0x10","-","Signal: External Blocking"]
["ThR","Blo TripCmd",164,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["ThR","ExBlo TripCmd",164,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["ThR","Alarm",164,1,"3","Bit","0x80","-","Signal: Alarm"]
["ThR","Trip (*)",164,1,"3","Bit","0x100","-","Signal: Trip"]
["ThR","TripCmd (*)",164,1,"3","Bit","0x200","-","Signal: Trip Command"]
["ThR","Alarm Pickup",164,1,"3","Bit","0x400","-","Signal: Alarm Pickup"]
["ThR","Alarm Timeout",164,1,"3","Bit","0x800","-","Signal: Alarm Timeout"]
["ThR","Load above SF",164,1,"3","Bit","0x1000","-","“Load above Service Factor”: If the current exceeds the set value of “UTC” (“Ultimate trip threshold”) then the used thermal capacity counts up and the state “Load above SF” is becoming true. If the current is below the “UTC” value this state is false."]
["ThR","RTD effective",164,1,"3","Bit","0x2000","-","This state becomes true if the following conditions are all fulfilled:\\n- the state “Load above SF” is true,\\n- the Winding Temperature Trip has been activated in the RTD module,\\n- for at least one temperature a valid value above 0°C (32°F) is being displayed."]
["TimeSync","synchronized",54,1,"3","Bit","0x1","-","Clock is synchronized."]
["URTD","Windg1 Superv",1007,1,"3","Bit","0x1","-","Signal: Windg1, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","Windg2 Superv",1007,1,"3","Bit","0x2","-","Signal: Windg2, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","Windg3 Superv",1007,1,"3","Bit","0x4","-","Signal: Windg3, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","Windg4 Superv",1007,1,"3","Bit","0x8","-","Signal: Windg4, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","Windg5 Superv",1007,1,"3","Bit","0x10","-","Signal: Windg5, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","Windg6 Superv",1007,1,"3","Bit","0x20","-","Signal: Windg6, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","MotBear1 Superv",1007,1,"3","Bit","0x40","-","Signal: MotBear1, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","MotBear2 Superv",1007,1,"3","Bit","0x80","-","Signal: MotBear2, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","LoadBear1 Superv",1007,1,"3","Bit","0x100","-","Signal: LoadBear1, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","LoadBear2 Superv",1007,1,"3","Bit","0x200","-","Signal: LoadBear2, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","Aux1 Superv",1007,1,"3","Bit","0x400","-","Signal: Aux1, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["URTD","Superv",1007,1,"3","Bit","0x800","-","Signal: URTD Channel Supervision. The value “1” reports a detected channel failure of at least one channel. (The value “0” means that all RTD channels are healthy.)"]
["URTD","Aux2 Superv",1007,1,"3","Bit","0x1000","-","Signal: Aux2, Channel Supervision. The value “1” reports a detected channel failure. (The value “0” means that this RTD channel is healthy.)"]
["V012[1]","ExBlo1-I",100,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V012[1]","ExBlo2-I",100,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V012[1]","ExBlo TripCmd-I",100,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V012[1]","Active",100,1,"3","Bit","0x8","-","Signal: active"]
["V012[1]","ExBlo",100,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V012[1]","Blo TripCmd",100,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V012[1]","ExBlo TripCmd",100,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V012[1]","Alarm",100,1,"3","Bit","0x80","-","Signal: Alarm voltage asymmetry"]
["V012[1]","Trip (*)",100,1,"3","Bit","0x100","-","Signal: Trip"]
["V012[1]","TripCmd (*)",100,1,"3","Bit","0x200","-","Signal: Trip Command"]
["V012[2]","ExBlo1-I",101,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V012[2]","ExBlo2-I",101,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V012[2]","ExBlo TripCmd-I",101,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V012[2]","Active",101,1,"3","Bit","0x8","-","Signal: active"]
["V012[2]","ExBlo",101,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V012[2]","Blo TripCmd",101,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V012[2]","ExBlo TripCmd",101,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V012[2]","Alarm",101,1,"3","Bit","0x80","-","Signal: Alarm voltage asymmetry"]
["V012[2]","Trip (*)",101,1,"3","Bit","0x100","-","Signal: Trip"]
["V012[2]","TripCmd (*)",101,1,"3","Bit","0x200","-","Signal: Trip Command"]
["V012[3]","ExBlo1-I",102,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V012[3]","ExBlo2-I",102,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V012[3]","ExBlo TripCmd-I",102,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V012[3]","Active",102,1,"3","Bit","0x8","-","Signal: active"]
["V012[3]","ExBlo",102,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V012[3]","Blo TripCmd",102,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V012[3]","ExBlo TripCmd",102,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V012[3]","Alarm",102,1,"3","Bit","0x80","-","Signal: Alarm voltage asymmetry"]
["V012[3]","Trip (*)",102,1,"3","Bit","0x100","-","Signal: Trip"]
["V012[3]","TripCmd (*)",102,1,"3","Bit","0x200","-","Signal: Trip Command"]
["V012[4]","ExBlo1-I",103,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V012[4]","ExBlo2-I",103,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V012[4]","ExBlo TripCmd-I",103,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V012[4]","Active",103,1,"3","Bit","0x8","-","Signal: active"]
["V012[4]","ExBlo",103,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V012[4]","Blo TripCmd",103,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V012[4]","ExBlo TripCmd",103,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V012[4]","Alarm",103,1,"3","Bit","0x80","-","Signal: Alarm voltage asymmetry"]
["V012[4]","Trip (*)",103,1,"3","Bit","0x100","-","Signal: Trip"]
["V012[4]","TripCmd (*)",103,1,"3","Bit","0x200","-","Signal: Trip Command"]
["V012[5]","ExBlo1-I",104,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V012[5]","ExBlo2-I",104,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V012[5]","ExBlo TripCmd-I",104,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V012[5]","Active",104,1,"3","Bit","0x8","-","Signal: active"]
["V012[5]","ExBlo",104,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V012[5]","Blo TripCmd",104,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V012[5]","ExBlo TripCmd",104,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V012[5]","Alarm",104,1,"3","Bit","0x80","-","Signal: Alarm voltage asymmetry"]
["V012[5]","Trip (*)",104,1,"3","Bit","0x100","-","Signal: Trip"]
["V012[5]","TripCmd (*)",104,1,"3","Bit","0x200","-","Signal: Trip Command"]
["V012[6]","ExBlo1-I",105,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V012[6]","ExBlo2-I",105,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V012[6]","ExBlo TripCmd-I",105,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V012[6]","Active",105,1,"3","Bit","0x8","-","Signal: active"]
["V012[6]","ExBlo",105,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V012[6]","Blo TripCmd",105,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V012[6]","ExBlo TripCmd",105,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V012[6]","Alarm",105,1,"3","Bit","0x80","-","Signal: Alarm voltage asymmetry"]
["V012[6]","Trip (*)",105,1,"3","Bit","0x100","-","Signal: Trip"]
["V012[6]","TripCmd (*)",105,1,"3","Bit","0x200","-","Signal: Trip Command"]
["VG[1]","ExBlo1-I",32,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["VG[1]","ExBlo2-I",32,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["VG[1]","ExBlo TripCmd-I",32,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["VG[1]","Active",32,1,"3","Bit","0x8","-","Signal: active"]
["VG[1]","ExBlo",32,1,"3","Bit","0x10","-","Signal: External Blocking"]
["VG[1]","Blo TripCmd",32,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["VG[1]","ExBlo TripCmd",32,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["VG[1]","Alarm",32,1,"3","Bit","0x80","-","Signal: Alarm Residual Voltage Supervision-stage"]
["VG[1]","Trip (*)",32,1,"3","Bit","0x100","-","Signal: Trip"]
["VG[1]","TripCmd (*)",32,1,"3","Bit","0x200","-","Signal: Trip Command"]
["VG[2]","ExBlo1-I",33,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["VG[2]","ExBlo2-I",33,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["VG[2]","ExBlo TripCmd-I",33,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["VG[2]","Active",33,1,"3","Bit","0x8","-","Signal: active"]
["VG[2]","ExBlo",33,1,"3","Bit","0x10","-","Signal: External Blocking"]
["VG[2]","Blo TripCmd",33,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["VG[2]","ExBlo TripCmd",33,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["VG[2]","Alarm",33,1,"3","Bit","0x80","-","Signal: Alarm Residual Voltage Supervision-stage"]
["VG[2]","Trip (*)",33,1,"3","Bit","0x100","-","Signal: Trip"]
["VG[2]","TripCmd (*)",33,1,"3","Bit","0x200","-","Signal: Trip Command"]
["V[1]","ExBlo1-I",24,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V[1]","ExBlo2-I",24,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V[1]","ExBlo TripCmd-I",24,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V[1]","Active",24,1,"3","Bit","0x8","-","Signal: active"]
["V[1]","ExBlo",24,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V[1]","Blo TripCmd",24,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V[1]","ExBlo TripCmd",24,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V[1]","Alarm L1",25,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["V[1]","Alarm L2",25,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["V[1]","Alarm L3",25,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["V[1]","Alarm",25,1,"3","Bit","0x8","-","Signal: Alarm voltage stage"]
["V[1]","Trip L1 (*)",25,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["V[1]","Trip L2 (*)",25,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["V[1]","Trip L3 (*)",25,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["V[1]","Trip (*)",25,1,"3","Bit","0x80","-","Signal: Trip"]
["V[1]","TripCmd (*)",25,1,"3","Bit","0x100","-","Signal: Trip Command"]
["V[1]","Imin release active",25,1,"3","Bit","0x200","-","Signal that the Imin release (minimum current) check is enabled and does not block the undervoltage detection at the moment."]
["V[2]","ExBlo1-I",26,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V[2]","ExBlo2-I",26,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V[2]","ExBlo TripCmd-I",26,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V[2]","Active",26,1,"3","Bit","0x8","-","Signal: active"]
["V[2]","ExBlo",26,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V[2]","Blo TripCmd",26,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V[2]","ExBlo TripCmd",26,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V[2]","Alarm L1",27,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["V[2]","Alarm L2",27,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["V[2]","Alarm L3",27,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["V[2]","Alarm",27,1,"3","Bit","0x8","-","Signal: Alarm voltage stage"]
["V[2]","Trip L1 (*)",27,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["V[2]","Trip L2 (*)",27,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["V[2]","Trip L3 (*)",27,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["V[2]","Trip (*)",27,1,"3","Bit","0x80","-","Signal: Trip"]
["V[2]","TripCmd (*)",27,1,"3","Bit","0x100","-","Signal: Trip Command"]
["V[2]","Imin release active",27,1,"3","Bit","0x200","-","Signal that the Imin release (minimum current) check is enabled and does not block the undervoltage detection at the moment."]
["V[3]","ExBlo1-I",28,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V[3]","ExBlo2-I",28,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V[3]","ExBlo TripCmd-I",28,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V[3]","Active",28,1,"3","Bit","0x8","-","Signal: active"]
["V[3]","ExBlo",28,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V[3]","Blo TripCmd",28,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V[3]","ExBlo TripCmd",28,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V[3]","Alarm L1",29,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["V[3]","Alarm L2",29,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["V[3]","Alarm L3",29,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["V[3]","Alarm",29,1,"3","Bit","0x8","-","Signal: Alarm voltage stage"]
["V[3]","Trip L1 (*)",29,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["V[3]","Trip L2 (*)",29,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["V[3]","Trip L3 (*)",29,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["V[3]","Trip (*)",29,1,"3","Bit","0x80","-","Signal: Trip"]
["V[3]","TripCmd (*)",29,1,"3","Bit","0x100","-","Signal: Trip Command"]
["V[3]","Imin release active",29,1,"3","Bit","0x200","-","Signal that the Imin release (minimum current) check is enabled and does not block the undervoltage detection at the moment."]
["V[4]","ExBlo1-I",30,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V[4]","ExBlo2-I",30,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V[4]","ExBlo TripCmd-I",30,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V[4]","Active",30,1,"3","Bit","0x8","-","Signal: active"]
["V[4]","ExBlo",30,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V[4]","Blo TripCmd",30,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V[4]","ExBlo TripCmd",30,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V[4]","Alarm L1",31,1,"3","Bit","0x1","-","Signal: Alarm L1"]
["V[4]","Alarm L2",31,1,"3","Bit","0x2","-","Signal: Alarm L2"]
["V[4]","Alarm L3",31,1,"3","Bit","0x4","-","Signal: Alarm L3"]
["V[4]","Alarm",31,1,"3","Bit","0x8","-","Signal: Alarm voltage stage"]
["V[4]","Trip L1 (*)",31,1,"3","Bit","0x10","-","Signal: General Trip Phase L1"]
["V[4]","Trip L2 (*)",31,1,"3","Bit","0x20","-","Signal: General Trip Phase L2"]
["V[4]","Trip L3 (*)",31,1,"3","Bit","0x40","-","Signal: General Trip Phase L3"]
["V[4]","Trip (*)",31,1,"3","Bit","0x80","-","Signal: Trip"]
["V[4]","TripCmd (*)",31,1,"3","Bit","0x100","-","Signal: Trip Command"]
["V[4]","Imin release active",31,1,"3","Bit","0x200","-","Signal that the Imin release (minimum current) check is enabled and does not block the undervoltage detection at the moment."]
["V[5]","ExBlo1-I",92,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V[5]","ExBlo2-I",92,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V[5]","ExBlo TripCmd-I",92,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V[5]","Active",92,1,"3","Bit","0x8","-","Signal: active"]
["V[5]","ExBlo",92,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V[5]","Blo TripCmd",92,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V[5]","ExBlo TripCmd",92,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V[5]","Alarm",92,1,"3","Bit","0x80","-","Signal: Alarm voltage stage"]
["V[5]","Alarm L1",92,1,"3","Bit","0x100","-","Signal: Alarm L1"]
["V[5]","Alarm L2",92,1,"3","Bit","0x200","-","Signal: Alarm L2"]
["V[5]","Alarm L3",92,1,"3","Bit","0x400","-","Signal: Alarm L3"]
["V[5]","Trip (*)",92,1,"3","Bit","0x800","-","Signal: Trip"]
["V[5]","Trip L1 (*)",92,1,"3","Bit","0x1000","-","Signal: General Trip Phase L1"]
["V[5]","Trip L2 (*)",92,1,"3","Bit","0x2000","-","Signal: General Trip Phase L2"]
["V[5]","Trip L3 (*)",92,1,"3","Bit","0x4000","-","Signal: General Trip Phase L3"]
["V[5]","TripCmd (*)",92,1,"3","Bit","0x8000","-","Signal: Trip Command"]
["V[5]","Imin release active",94,1,"3","Bit","0x1","-","Signal that the Imin release (minimum current) check is enabled and does not block the undervoltage detection at the moment."]
["V[6]","ExBlo1-I",93,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["V[6]","ExBlo2-I",93,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["V[6]","ExBlo TripCmd-I",93,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["V[6]","Active",93,1,"3","Bit","0x8","-","Signal: active"]
["V[6]","ExBlo",93,1,"3","Bit","0x10","-","Signal: External Blocking"]
["V[6]","Blo TripCmd",93,1,"3","Bit","0x20","-","Signal: Trip Command blocked"]
["V[6]","ExBlo TripCmd",93,1,"3","Bit","0x40","-","Signal: External Blocking of the Trip Command"]
["V[6]","Alarm",93,1,"3","Bit","0x80","-","Signal: Alarm voltage stage"]
["V[6]","Alarm L1",93,1,"3","Bit","0x100","-","Signal: Alarm L1"]
["V[6]","Alarm L2",93,1,"3","Bit","0x200","-","Signal: Alarm L2"]
["V[6]","Alarm L3",93,1,"3","Bit","0x400","-","Signal: Alarm L3"]
["V[6]","Trip (*)",93,1,"3","Bit","0x800","-","Signal: Trip"]
["V[6]","Trip L1 (*)",93,1,"3","Bit","0x1000","-","Signal: General Trip Phase L1"]
["V[6]","Trip L2 (*)",93,1,"3","Bit","0x2000","-","Signal: General Trip Phase L2"]
["V[6]","Trip L3 (*)",93,1,"3","Bit","0x4000","-","Signal: General Trip Phase L3"]
["V[6]","TripCmd (*)",93,1,"3","Bit","0x8000","-","Signal: Trip Command"]
["V[6]","Imin release active",95,1,"3","Bit","0x1","-","Signal that the Imin release (minimum current) check is enabled and does not block the undervoltage detection at the moment."]
["f[1]","ExBlo1-I",34,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["f[1]","ExBlo2-I",34,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["f[1]","ExBlo TripCmd-I",34,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["f[1]","Active",34,1,"3","Bit","0x8","-","Signal: active"]
["f[1]","ExBlo",34,1,"3","Bit","0x10","-","Signal: External Blocking"]
["f[1]","Blo by V<",34,1,"3","Bit","0x20","-","Signal: Module is blocked by undervoltage."]
["f[1]","Blo TripCmd",34,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["f[1]","ExBlo TripCmd",34,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["f[1]","Alarm f",35,1,"3","Bit","0x1","-","Signal: Alarm Frequency Protection"]
["f[1]","Alarm df/dt | DF/DT",35,1,"3","Bit","0x2","-","Alarm instantaneous or average value of the rate-of-frequency-change "]
["f[1]","Trip f (*)",35,1,"3","Bit","0x4","-","Signal: Frequency has exceeded the limit."]
["f[1]","Trip df/dt | DF/DT (*)",35,1,"3","Bit","0x8","-","Signal: Trip df/dt or DF/DT"]
["f[1]","Alarm",35,1,"3","Bit","0x10","-","Signal: Alarm Frequency Protection (collective signal)"]
["f[1]","Alarm delta phi",35,1,"3","Bit","0x20","-","Signal: Alarm Vector Surge"]
["f[1]","Trip (*)",35,1,"3","Bit","0x40","-","Signal: Trip Frequency Protection (collective signal)"]
["f[1]","Trip delta phi (*)",35,1,"3","Bit","0x80","-","Signal: Trip Vector Surge"]
["f[1]","TripCmd (*)",35,1,"3","Bit","0x100","-","Signal: Trip Command"]
["f[2]","ExBlo1-I",36,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["f[2]","ExBlo2-I",36,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["f[2]","ExBlo TripCmd-I",36,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["f[2]","Active",36,1,"3","Bit","0x8","-","Signal: active"]
["f[2]","ExBlo",36,1,"3","Bit","0x10","-","Signal: External Blocking"]
["f[2]","Blo by V<",36,1,"3","Bit","0x20","-","Signal: Module is blocked by undervoltage."]
["f[2]","Blo TripCmd",36,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["f[2]","ExBlo TripCmd",36,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["f[2]","Alarm f",37,1,"3","Bit","0x1","-","Signal: Alarm Frequency Protection"]
["f[2]","Alarm df/dt | DF/DT",37,1,"3","Bit","0x2","-","Alarm instantaneous or average value of the rate-of-frequency-change "]
["f[2]","Trip f (*)",37,1,"3","Bit","0x4","-","Signal: Frequency has exceeded the limit."]
["f[2]","Trip df/dt | DF/DT (*)",37,1,"3","Bit","0x8","-","Signal: Trip df/dt or DF/DT"]
["f[2]","Alarm",37,1,"3","Bit","0x10","-","Signal: Alarm Frequency Protection (collective signal)"]
["f[2]","Alarm delta phi",37,1,"3","Bit","0x20","-","Signal: Alarm Vector Surge"]
["f[2]","Trip (*)",37,1,"3","Bit","0x40","-","Signal: Trip Frequency Protection (collective signal)"]
["f[2]","Trip delta phi (*)",37,1,"3","Bit","0x80","-","Signal: Trip Vector Surge"]
["f[2]","TripCmd (*)",37,1,"3","Bit","0x100","-","Signal: Trip Command"]
["f[3]","ExBlo1-I",38,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["f[3]","ExBlo2-I",38,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["f[3]","ExBlo TripCmd-I",38,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["f[3]","Active",38,1,"3","Bit","0x8","-","Signal: active"]
["f[3]","ExBlo",38,1,"3","Bit","0x10","-","Signal: External Blocking"]
["f[3]","Blo by V<",38,1,"3","Bit","0x20","-","Signal: Module is blocked by undervoltage."]
["f[3]","Blo TripCmd",38,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["f[3]","ExBlo TripCmd",38,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["f[3]","Alarm f",39,1,"3","Bit","0x1","-","Signal: Alarm Frequency Protection"]
["f[3]","Alarm df/dt | DF/DT",39,1,"3","Bit","0x2","-","Alarm instantaneous or average value of the rate-of-frequency-change "]
["f[3]","Trip f (*)",39,1,"3","Bit","0x4","-","Signal: Frequency has exceeded the limit."]
["f[3]","Trip df/dt | DF/DT (*)",39,1,"3","Bit","0x8","-","Signal: Trip df/dt or DF/DT"]
["f[3]","Alarm",39,1,"3","Bit","0x10","-","Signal: Alarm Frequency Protection (collective signal)"]
["f[3]","Alarm delta phi",39,1,"3","Bit","0x20","-","Signal: Alarm Vector Surge"]
["f[3]","Trip (*)",39,1,"3","Bit","0x40","-","Signal: Trip Frequency Protection (collective signal)"]
["f[3]","Trip delta phi (*)",39,1,"3","Bit","0x80","-","Signal: Trip Vector Surge"]
["f[3]","TripCmd (*)",39,1,"3","Bit","0x100","-","Signal: Trip Command"]
["f[4]","ExBlo1-I",40,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["f[4]","ExBlo2-I",40,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["f[4]","ExBlo TripCmd-I",40,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["f[4]","Active",40,1,"3","Bit","0x8","-","Signal: active"]
["f[4]","ExBlo",40,1,"3","Bit","0x10","-","Signal: External Blocking"]
["f[4]","Blo by V<",40,1,"3","Bit","0x20","-","Signal: Module is blocked by undervoltage."]
["f[4]","Blo TripCmd",40,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["f[4]","ExBlo TripCmd",40,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["f[4]","Alarm f",41,1,"3","Bit","0x1","-","Signal: Alarm Frequency Protection"]
["f[4]","Alarm df/dt | DF/DT",41,1,"3","Bit","0x2","-","Alarm instantaneous or average value of the rate-of-frequency-change "]
["f[4]","Trip f (*)",41,1,"3","Bit","0x4","-","Signal: Frequency has exceeded the limit."]
["f[4]","Trip df/dt | DF/DT (*)",41,1,"3","Bit","0x8","-","Signal: Trip df/dt or DF/DT"]
["f[4]","Alarm",41,1,"3","Bit","0x10","-","Signal: Alarm Frequency Protection (collective signal)"]
["f[4]","Alarm delta phi",41,1,"3","Bit","0x20","-","Signal: Alarm Vector Surge"]
["f[4]","Trip (*)",41,1,"3","Bit","0x40","-","Signal: Trip Frequency Protection (collective signal)"]
["f[4]","Trip delta phi (*)",41,1,"3","Bit","0x80","-","Signal: Trip Vector Surge"]
["f[4]","TripCmd (*)",41,1,"3","Bit","0x100","-","Signal: Trip Command"]
["f[5]","ExBlo1-I",42,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["f[5]","ExBlo2-I",42,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["f[5]","ExBlo TripCmd-I",42,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["f[5]","Active",42,1,"3","Bit","0x8","-","Signal: active"]
["f[5]","ExBlo",42,1,"3","Bit","0x10","-","Signal: External Blocking"]
["f[5]","Blo by V<",42,1,"3","Bit","0x20","-","Signal: Module is blocked by undervoltage."]
["f[5]","Blo TripCmd",42,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["f[5]","ExBlo TripCmd",42,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["f[5]","Alarm f",43,1,"3","Bit","0x1","-","Signal: Alarm Frequency Protection"]
["f[5]","Alarm df/dt | DF/DT",43,1,"3","Bit","0x2","-","Alarm instantaneous or average value of the rate-of-frequency-change "]
["f[5]","Trip f (*)",43,1,"3","Bit","0x4","-","Signal: Frequency has exceeded the limit."]
["f[5]","Trip df/dt | DF/DT (*)",43,1,"3","Bit","0x8","-","Signal: Trip df/dt or DF/DT"]
["f[5]","Alarm",43,1,"3","Bit","0x10","-","Signal: Alarm Frequency Protection (collective signal)"]
["f[5]","Alarm delta phi",43,1,"3","Bit","0x20","-","Signal: Alarm Vector Surge"]
["f[5]","Trip (*)",43,1,"3","Bit","0x40","-","Signal: Trip Frequency Protection (collective signal)"]
["f[5]","Trip delta phi (*)",43,1,"3","Bit","0x80","-","Signal: Trip Vector Surge"]
["f[5]","TripCmd (*)",43,1,"3","Bit","0x100","-","Signal: Trip Command"]
["f[6]","ExBlo1-I",44,1,"3","Bit","0x1","-","Module input state: External blocking1"]
["f[6]","ExBlo2-I",44,1,"3","Bit","0x2","-","Module input state: External blocking2"]
["f[6]","ExBlo TripCmd-I",44,1,"3","Bit","0x4","-","Module input state: External Blocking of the Trip Command"]
["f[6]","Active",44,1,"3","Bit","0x8","-","Signal: active"]
["f[6]","ExBlo",44,1,"3","Bit","0x10","-","Signal: External Blocking"]
["f[6]","Blo by V<",44,1,"3","Bit","0x20","-","Signal: Module is blocked by undervoltage."]
["f[6]","Blo TripCmd",44,1,"3","Bit","0x40","-","Signal: Trip Command blocked"]
["f[6]","ExBlo TripCmd",44,1,"3","Bit","0x80","-","Signal: External Blocking of the Trip Command"]
["f[6]","Alarm f",45,1,"3","Bit","0x1","-","Signal: Alarm Frequency Protection"]
["f[6]","Alarm df/dt | DF/DT",45,1,"3","Bit","0x2","-","Alarm instantaneous or average value of the rate-of-frequency-change "]
["f[6]","Trip f (*)",45,1,"3","Bit","0x4","-","Signal: Frequency has exceeded the limit."]
["f[6]","Trip df/dt | DF/DT (*)",45,1,"3","Bit","0x8","-","Signal: Trip df/dt or DF/DT"]
["f[6]","Alarm",45,1,"3","Bit","0x10","-","Signal: Alarm Frequency Protection (collective signal)"]
["f[6]","Alarm delta phi",45,1,"3","Bit","0x20","-","Signal: Alarm Vector Surge"]
["f[6]","Trip (*)",45,1,"3","Bit","0x40","-","Signal: Trip Frequency Protection (collective signal)"]
["f[6]","Trip delta phi (*)",45,1,"3","Bit","0x80","-","Signal: Trip Vector Surge"]
["f[6]","TripCmd (*)",45,1,"3","Bit","0x100","-","Signal: Trip Command"]

{"sheet":"Adjust","index":2,"n_rows":13,"n_cols":9,"rows_kept":13,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["Date and Time","y",32500,6,"3 16","Short","Word 0","-","year"]
["Date and Time","m",32500,6,"3 16","Short","Word 1","-","month"]
["Date and Time","d",32500,6,"3 16","Short","Word 2","-","days"]
["Date and Time","h",32500,6,"3 16","Short","Word 3","-","hours"]
["Date and Time","min",32500,6,"3 16","Short","Word 4","-","minute"]
["Date and Time","ms",32500,6,"3 16","Short","Word 5","-","milliseconds"]
["Fault rec","RecordNo",50000,9,"3 16","Short","Word 0","-","Record Number"]
["Fault rec","Trip Cause",50000,9,"3 16","Short","Word 1","-","Code for the trip cause. In case of several simultaneous trip causes the primary cause is selected. If there is another trip later then the new trip cause overwrites the previous one. The codes for the trip cause are documented in the SCADA documentation."]
["Fault rec","Pickup Cause",50000,9,"3 16","Short","Word 2","-","Code for last PickUp cause corresponds to fault record: See scada doc for correlation between pickup reason and code"]
["Fault rec","Fault No.",50000,9,"3 16","Short","Word 3","-","Fault number"]
["Fault rec","No. of Grid Faults",50000,9,"3 16","Short","Word 4","-","Number of grid faults: This is a counter for all faults (i.e. General Alarms »Prot . Alarm«), but except faults during a running cycle of the Automatic Reclosure module (signal »AR . running«). (Remark: The »Fault No.« counts every new fault independent of AR cycles. This means that for protective devices without AR module these two counters are equivalent.)"]
["Fault rec","Time stamp:",50000,9,"3 16","long long","Word 5- Word 8","-","Timestamp in milliseconds since 1970"]

{"sheet":"Command","index":3,"n_rows":38,"n_cols":9,"rows_kept":38,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["Acknowledge","LEDs",22000,1,"5","0xFF00","Word 0","-","LEDs"]
["Acknowledge","Binary Outputs",22001,1,"5","0xFF00","Word 0","-","Binary Outputs"]
["Acknowledge","Scada",22002,1,"5","0xFF00","Word 0","-","Scada"]
["Acknowledge","Device",22003,1,"5","0xFF00","Word 0","-","Device"]
["Acknowledge","Ack TripCmd",22005,1,"5","0xFF00","Word 0","-","Signal: Acknowledge Trip Command"]
["Reset","Modbus diagnosis counter",22006,1,"5","0xFF00","Word 0","-","Modbus diagnosis counter"]
["Reset","Res all Energy Cr",22011,1,"5","0xFF00","Word 0","-","Reset of all Energy Counters"]
["Reset","Res Sum trip",22012,1,"5","0xFF00","Word 0","-","Reset summation of the tripping currents"]
["Scada Cmd","Assbl Scada Cmd 1",22020,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 2",22021,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 3",22022,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 4",22023,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 5",22024,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 6",22025,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 7",22026,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 8",22027,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 9",22028,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 10",22029,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 11",22030,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 12",22031,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 13",22032,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 14",22033,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 15",22034,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Scada Cmd","Assbl Scada Cmd 16",22035,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Assignable Scada Command"]
["Fault rec","Res all rec",22040,1,"5","0xFF00","Word 0","-","Reset all records"]
["PSet-Switch","Scada PS1",22050,1,"5","0xFF00","Word 0","-","Scada Setting Group1"]
["PSet-Switch","Scada PS2",22051,1,"5","0xFF00","Word 0","-","Scada Setting Group2"]
["PSet-Switch","Scada PS3",22052,1,"5","0xFF00","Word 0","-","Scada Setting Group3"]
["PSet-Switch","Scada PS4",22053,1,"5","0xFF00","Word 0","-","Scada Setting Group4"]
["Maint Mode","Maint Mode SCADA",22054,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Signal: Arc Flash Reduction Maintenance SCADA Mode"]
["Res I2T Used","Res I2T Used",22055,1,"5","0xFF00","Word 0","-","Reset thermal capacity used."]
["Res OperationsCr","Res OperationsCr",22056,1,"5","0xFF00","Word 0","-","Reset all counters in history group operations"]
["Res AlarmCr","Res AlarmCr",22057,1,"5","0xFF00","Word 0","-","Reset all counters in history group alarms"]
["Res TripCmdCr","Res TripCmdCr",22058,1,"5","0xFF00","Word 0","-","Reset all counters in history group Trip Commands"]
["Res TotalCr","Res TotalCr",22059,1,"5","0xFF00","Word 0","-","Reset all counters in history group total"]
["Res All","Res All",22060,1,"5","0xFF00","Word 0","-","Reset of all Counters"]
["SG","SG ControlCmd1",22100,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Control Command Switchgear"]

{"sheet":"Measure","index":4,"n_rows":440,"n_cols":9,"rows_kept":440,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["CT","IL1 ",20100,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (fundamental)"]
["CT","IL2 ",20102,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (fundamental)"]
["CT","IL3 ",20104,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (fundamental)"]
["CT","IG meas ",20106,2,"4","Float IEE754","Word 0","A","Measured value (measured): IG (fundamental)"]
["CT","I0 ",20114,2,"4","Float IEE754","Word 0","A","Measured value (calculated): Zero current (fundamental)"]
["CT","I1 ",20116,2,"4","Float IEE754","Word 0","A","Measured value (calculated): Positive phase sequence current (fundamental)"]
["CT","I2 ",20118,2,"4","Float IEE754","Word 0","A","Measured value (calculated): Unbalanced load current (fundamental)"]
["CT","IG calc ",20160,2,"4","Float IEE754","Word 0","A","Measured value (calculated): IG (fundamental)"]
["CT","phi IG calc",20200,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IG calc\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["CT","phi IG meas",20202,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IG meas\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["CT","phi IL1",20204,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IL1\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["CT","phi IL2",20206,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IL2\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["CT","phi IL3",20208,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IL3\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["CT","IL1 THD",20210,2,"4","Float IEE754","Word 0","A","Measured value (calculated): IL1 Total Harmonic Current "]
["CT","IL2 THD",20212,2,"4","Float IEE754","Word 0","A","Measured value (calculated): IL2 Total Harmonic Current "]
["CT","IL3 THD",20214,2,"4","Float IEE754","Word 0","A","Measured value (calculated): IL3 Total Harmonic Current "]
["CT","%IL1 THD",20216,2,"4","Float IEE754","Word 0","%","Measured value (calculated): IL1 Total Harmonic Distortion"]
["CT","%IL2 THD",20218,2,"4","Float IEE754","Word 0","%","Measured value (calculated): IL2 Total Harmonic Distortion"]
["CT","%IL3 THD",20220,2,"4","Float IEE754","Word 0","%","Measured value (calculated): IL3 Total Harmonic Distortion"]
["CT","IL1 RMS",20316,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (RMS)"]
["CT","IL2 RMS",20318,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (RMS)"]
["CT","IL3 RMS",20320,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (RMS)"]
["CT","IG meas RMS",20322,2,"4","Float IEE754","Word 0","A","Measured value (measured): IG (RMS)"]
["CT","IG calc RMS",20324,2,"4","Float IEE754","Word 0","A","Measured value (calculated): IG (RMS)"]
["CT","%(I2/I1)",20376,2,"4","Float IEE754","Word 0","%","Measured value (calculated): I2/I1, phase sequence will be taken into account automatically."]
["CT","phi I0",20378,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle Zero Sequence System\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["CT","phi I1",20380,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Positive Sequence System\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["CT","phi I2",20382,2,"4","Float IEE754","Word 0","°","Measured Value (calculated): Angle of Negative Sequence System\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["CT","I1 max ",21074,2,"4","Float IEE754","Word 0","A","Maximum value positive phase sequence current (fundamental)"]
["CT","I1 min ",21076,2,"4","Float IEE754","Word 0","A","Minimum value positive phase sequence current (fundamental)"]
["CT","I2 max ",21080,2,"4","Float IEE754","Word 0","A","Maximum value negative sequence current (fundamental)"]
["CT","I2 min  ",21082,2,"4","Float IEE754","Word 0","A","Minimum value unbalanced load current (fundamental)"]
["CT","IL1 avg RMS",21130,2,"4","Float IEE754","Word 0","A","IL1 average value (RMS)"]
["CT","IL2 avg RMS",21132,2,"4","Float IEE754","Word 0","A","IL2 average value (RMS)"]
["CT","IL3 avg RMS",21134,2,"4","Float IEE754","Word 0","A","IL3 average value (RMS)"]
["CT","IL1 max RMS",21136,2,"4","Float IEE754","Word 0","A","IL1 maximum value (RMS)"]
["CT","IL2 max RMS",21138,2,"4","Float IEE754","Word 0","A","IL2 maximum value (RMS)"]
["CT","IL3 max RMS",21140,2,"4","Float IEE754","Word 0","A","IL3 maximum value (RMS)"]
["CT","IL1 min  RMS",21142,2,"4","Float IEE754","Word 0","A","IL1 minimum value  (RMS)"]
["CT","IL2 min  RMS",21144,2,"4","Float IEE754","Word 0","A","IL2 minimum value  (RMS)"]
["CT","IL3 min  RMS",21146,2,"4","Float IEE754","Word 0","A","IL3 minimum value  (RMS)"]
["CT","IG calc max RMS",21456,2,"4","Float IEE754","Word 0","A","Measured value (calculated):IG maximum value (RMS)"]
["CT","IG calc min  RMS",21458,2,"4","Float IEE754","Word 0","A","Measured value (calculated):IG minimum value  (RMS)"]
["CT","IG meas max RMS",21462,2,"4","Float IEE754","Word 0","A","Measured value: IG maximum value (RMS)"]
["CT","IG meas min  RMS",21464,2,"4","Float IEE754","Word 0","A","Measured value: IG minimum value  (RMS)"]
["CT","%(I2/I1)  max",21468,2,"4","Float IEE754","Word 0","%","Measured value (calculated): I2/I1 maximum value, phase sequence will be taken into account automatically"]
["CT","%(I2/I1)  min",21470,2,"4","Float IEE754","Word 0","%","Measured value (calculated): I2/I1 minimum value, phase sequence will be taken into account automatically"]
["CT","IL1 Peak (Demand)",21784,2,"4","Float IEE754","Word 0","A","IL1 Peak value, RMS value"]
["CT","IL2 Peak (Demand)",21786,2,"4","Float IEE754","Word 0","A","IL2 Peak value, RMS value"]
["CT","IL3 Peak (Demand)",21788,2,"4","Float IEE754","Word 0","A","IL3 Peak value, RMS value"]
["CT - fault value","IL1 ",50100,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (fundamental) , as stored in the Fault Recorder"]
["CT - fault value","IL2 ",50102,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (fundamental) , as stored in the Fault Recorder"]
["CT - fault value","IL3 ",50104,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (fundamental) , as stored in the Fault Recorder"]
["CT - fault value","IG meas ",50106,2,"4","Float IEE754","Word 0","A","Measured value (measured): IG (fundamental) , as stored in the Fault Recorder"]
["CT - fault value","I0 ",50114,2,"4","Float IEE754","Word 0","A","Measured value (calculated): Zero current (fundamental) , as stored in the Fault Recorder"]
["CT - fault value","I1 ",50116,2,"4","Float IEE754","Word 0","A","Measured value (calculated): Positive phase sequence current (fundamental) , as stored in the Fault Recorder"]
["CT - fault value","I2 ",50118,2,"4","Float IEE754","Word 0","A","Measured value (calculated): Unbalanced load current (fundamental) , as stored in the Fault Recorder"]
["CT - fault value","IG calc ",50160,2,"4","Float IEE754","Word 0","A","Measured value (calculated): IG (fundamental) , as stored in the Fault Recorder"]
["CT - fault value","phi IG calc",50200,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IG calc\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["CT - fault value","phi IG meas",50202,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IG meas\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["CT - fault value","phi IL1",50204,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IL1\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["CT - fault value","phi IL2",50206,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IL2\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["CT - fault value","phi IL3",50208,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor IL3\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["CT - fault value","IL1 RMS",50316,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (RMS) , as stored in the Fault Recorder"]
["CT - fault value","IL2 RMS",50318,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (RMS) , as stored in the Fault Recorder"]
["CT - fault value","IL3 RMS",50320,2,"4","Float IEE754","Word 0","A","Measured value: Phase current (RMS) , as stored in the Fault Recorder"]
["CT - fault value","IG meas RMS",50322,2,"4","Float IEE754","Word 0","A","Measured value (measured): IG (RMS) , as stored in the Fault Recorder"]
["CT - fault value","IG calc RMS",50324,2,"4","Float IEE754","Word 0","A","Measured value (calculated): IG (RMS) , as stored in the Fault Recorder"]
["CT - fault value","%(I2/I1)",50376,2,"4","Float IEE754","Word 0","%","Measured value (calculated): I2/I1, phase sequence will be taken into account automatically. , as stored in the Fault Recorder"]
["Date and Time","y",20000,6,"4","Short","Word 0","-","year"]
["Date and Time","m",20000,6,"4","Short","Word 1","-","month"]
["Date and Time","d",20000,6,"4","Short","Word 2","-","days"]
["Date and Time","h",20000,6,"4","Short","Word 3","-","hours"]
["Date and Time","min",20000,6,"4","Short","Word 4","-","minute"]
["Date and Time","ms",20000,6,"4","Short","Word 5","-","milliseconds"]
["ExP[1]","NumberOfAlarms",24018,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["ExP[1]","NumberOfTripCmds",24020,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["ExP[2]","NumberOfAlarms",24022,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["ExP[2]","NumberOfTripCmds",24024,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["ExP[3]","NumberOfAlarms",24026,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["ExP[3]","NumberOfTripCmds",24028,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["ExP[4]","NumberOfAlarms",24030,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["ExP[4]","NumberOfTripCmds",24032,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I2>[1]","nRevTrips",21614,2,"4","Float IEE754","Word 0","-","Number of reverse spinning trips since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["I2>[1]","NumberOfAlarms",21724,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I2>[1]","NumberOfTripCmds",21726,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I2>[2]","NumberOfAlarms",21730,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I2>[2]","NumberOfTripCmds",21732,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I<[1]","NumberOfTripCmds",21642,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I<[1]","NumberOfAlarms",21648,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I<[2]","NumberOfTripCmds",21644,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I<[2]","NumberOfAlarms",21650,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I<[3]","NumberOfTripCmds",21646,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I<[3]","NumberOfAlarms",21652,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["IG[1]","NumberOfAlarms",21690,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["IG[1]","NumberOfTripCmds",21692,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["IG[2]","NumberOfAlarms",21694,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["IG[2]","NumberOfTripCmds",21696,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["IG[3]","NumberOfAlarms",21698,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["IG[3]","NumberOfTripCmds",21700,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["IG[4]","NumberOfAlarms",21702,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["IG[4]","NumberOfTripCmds",21704,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["IRIG-B","Edges",20298,2,"4","Float IEE754","Word 0","-","Edges: Total number of rising and falling edges. This signal indicates if a signal is available at the IRIG-B input."]
["IRIG-B","NoOfFrameErrors",20300,2,"4","Float IEE754","Word 0","-","Total Number of Frame Errors.  Physically corrupted Frame."]
["IRIG-B","NoOfFramesOK",20302,2,"4","Float IEE754","Word 0","-","Total Number valid Frames."]
["I[1]","NumberOfAlarms",21666,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I[1]","NumberOfTripCmds",21668,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I[2]","NumberOfAlarms",21670,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I[2]","NumberOfTripCmds",21672,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I[3]","NumberOfAlarms",21674,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I[3]","NumberOfTripCmds",21676,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I[4]","NumberOfAlarms",21678,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I[4]","NumberOfTripCmds",21680,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I[5]","NumberOfAlarms",21682,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I[5]","NumberOfTripCmds",21684,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["I[6]","NumberOfAlarms",21686,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["I[6]","NumberOfTripCmds",21688,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["Jam[1]","NumberOfTripCmds",21580,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["Jam[1]","NumberOfAlarms",21662,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["Jam[2]","NumberOfTripCmds",21582,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["Jam[2]","NumberOfAlarms",21664,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["MStart","ABK Rem.Time",20466,2,"4","Float IEE754","Word 0","s","This is the remaining anti-backspin time."]
["MStart","IL1 Ib",20468,2,"4","Float IEE754","Word 0","Ib","Measured value: Phase current as multiple of Ib"]
["MStart","IL2 Ib",20470,2,"4","Float IEE754","Word 0","Ib","Measured value: Phase current as multiple of Ib"]
["MStart","IL3 Ib",20472,2,"4","Float IEE754","Word 0","Ib","Measured value: Phase current as multiple of Ib"]
["MStart","NOCS Remaining",20474,2,"4","Float IEE754","Word 0","-","This counter shows the number of remaining permitted cold starts."]
["MStart","SPH Remaining",20476,2,"4","Float IEE754","Word 0","-","SPH Remaining"]
["MStart","TBS Rem.Block.Time",20478,2,"4","Float IEE754","Word 0","s","In case that the Motor is blocked by TBS functions, the remaining blocking time is shown."]
["MStart","I3 PRMS avg",20510,2,"4","Float IEE754","Word 0","A","Average RMS current of all 3 phases"]
["MStart","I3 P (%Ib) avg",20512,2,"4","Float IEE754","Word 0","Ib","Average RMS current of all 3 phases as percentages of Ib"]
["MStart","SPH Rem.Block.Time",20894,2,"4","Float IEE754","Word 0","min","In case that the Motor is blocked by an SPH blocking, the remaining blocking time is shown until the next motor start is permitted."]
["MStart","HighestRunI",21584,2,"4","Float IEE754","Word 0","A","Highest running phase current. The time stamp indicates the point in time when the maximum current has occurred. Resettable with »Sys . Res OperationsCr« or »Sys . Res All«."]
["MStart","HighestStartI",21586,2,"4","Float IEE754","Word 0","A","Highest starting phase current. The time stamp indicates the point in time when the maximum current has occurred. Resettable with »Sys . Res OperationsCr« or »Sys . Res All«."]
["MStart","OCNT",21588,2,"4","Float IEE754","Word 0","-","Motor Operation count since last reset. Resettable with »Sys . Res OperationsCr« or »Sys . Res All«."]
["MStart","RunTime",21590,2,"4","Float IEE754","Word 0","h","Motor Operation time since last reset. Resettable with »Sys . Res OperationsCr« or »Sys . Res All«."]
["MStart","TOCS",21592,2,"4","Float IEE754","Word 0","-","Total Motor Operation count since last reset. Resettable with »Sys . Res TotalCr« or »Sys . Res All«."]
["MStart","TRunTime",21594,2,"4","Float IEE754","Word 0","h","Motor Operation (Motor run time) time since last reset. Resettable with »Sys . Res TotalCr« or »Sys . Res All«."]
["MStart","nEmrgOvr",21596,2,"4","Float IEE754","Word 0","-","Number of emergency overrides since last reset. Resettable with »Sys . Res OperationsCr« or »Sys . Res All«."]
["MStart","nInSqTrips",21598,2,"4","Float IEE754","Word 0","-","Number of incomplete sequence trips since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["MStart","nTRNTrips",21606,2,"4","Float IEE754","Word 0","-","Number of transition trips since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["MStart","nZSWTrips",21608,2,"4","Float IEE754","Word 0","-","Number of zero speed switch trips since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["MStart","nSPHBlocks",21654,2,"4","Float IEE754","Word 0","-","Number of start per hour blocks since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["MStart","nTBSBlocks",21656,2,"4","Float IEE754","Word 0","-","Number of time between start blocks since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["MStart","Highest%I2/I1",21722,2,"4","Float IEE754","Word 0","%","Highest %I2/I1 value since last reset. The time stamp indicates the point in time when the maximum unbalanced load has occurred. Resettable with »Sys . Res OperationsCr« or »Sys . Res All«."]
["MStart","I3P Fla Demand",21734,2,"4","Float IEE754","Word 0","Ib","RMS current of all 3 phases calculated in a fixed demand window as percentages of Ib"]
["MStart","IL1 avg Ib",21736,2,"4","Float IEE754","Word 0","Ib","IL1 average value as multiple of Ib"]
["MStart","IL1 max Ib",21738,2,"4","Float IEE754","Word 0","Ib","IL1 maximum value as multiple of Ib"]
["MStart","IL1 min  Ib",21740,2,"4","Float IEE754","Word 0","Ib","IL1 minimum value  as multiple of Ib"]
["MStart","IL2 avg Ib",21742,2,"4","Float IEE754","Word 0","Ib","IL2 average value as multiple of Ib"]
["MStart","IL2 max Ib",21744,2,"4","Float IEE754","Word 0","Ib","IL2 maximum value as multiple of Ib"]
["MStart","IL2 min  Ib",21746,2,"4","Float IEE754","Word 0","Ib","IL2 minimum value  as multiple of Ib"]
["MStart","IL3 avg Ib",21748,2,"4","Float IEE754","Word 0","Ib","IL3 average value as multiple of Ib"]
["MStart","IL3 max Ib",21750,2,"4","Float IEE754","Word 0","Ib","IL3 maximum value as multiple of Ib"]
["MStart","IL3 min  Ib",21752,2,"4","Float IEE754","Word 0","Ib","IL3 minimum value  as multiple of Ib"]
["MStart - fault value","I3 PRMS avg",50510,2,"4","Float IEE754","Word 0","A","Average RMS current of all 3 phases , as stored in the Fault Recorder"]
["Modbus","Mapped Meas 1",23000,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 2",23002,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 3",23004,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 4",23006,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 5",23008,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 6",23010,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 7",23012,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 8",23014,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 9",23016,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 10",23018,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 11",23020,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 12",23022,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 13",23024,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 14",23026,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 15",23028,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["Modbus","Mapped Meas 16",23030,2,"4","Float IEE754","Word 0","-","Mapped Measured Values. They can be used to provide measured values to the Modbus Master."]
["PF[1]","NumberOfAlarms",20630,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["PF[1]","NumberOfTripCmds",20632,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["PF[2]","NumberOfAlarms",20634,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["PF[2]","NumberOfTripCmds",20636,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["PQSCr","cos phi ",20152,2,"4","Float IEE754","Word 0","-","Measured value (calculated): Power factor: Sign Convention: sign(PF) = sign(P )"]
["PQSCr","P  ",20154,2,"4","Float IEE754","Word 0","W","Measured value (calculated): Active power (P- = Fed Active Power, P+ = Consumpted Active Power) (fundamental)"]
["PQSCr","Q  ",20156,2,"4","Float IEE754","Word 0","VAr","Measured value (calculated): Reactive power (Q- = Fed Reactive Power, Q+ = Consumpted Reactive Power) (fundamental)"]
["PQSCr","S  ",20158,2,"4","Float IEE754","Word 0","VA","Measured Value (Calculated): Apparent power (fundamental)"]
["PQSCr","Wp+",20174,2,"4","Float IEE754","Word 0","kWh","Positive Active Power is consumed active energy "]
["PQSCr","Wp-",20176,2,"4","Float IEE754","Word 0","kWh","Negative Active Power (Fed Energy)"]
["PQSCr","Wq+",20178,2,"4","Float IEE754","Word 0","kVArh","Positive Reactive Power is consumed Reactive Energy"]
["PQSCr","Wq-",20180,2,"4","Float IEE754","Word 0","kVArh","Negative Reactive Power (Fed Energy)"]
["PQSCr","P  RMS",20452,2,"4","Float IEE754","Word 0","W","Measured value (calculated): Active power (P- = Fed Active Power, P+ = Consumpted Active Power) (RMS)"]
["PQSCr","S  RMS",20454,2,"4","Float IEE754","Word 0","VA","Measured Value (Calculated): Apparent power (RMS)"]
["PQSCr","cos phi RMS",20456,2,"4","Float IEE754","Word 0","-","Measured value (calculated): Power factor: Sign Convention: sign(PF) = sign(P )"]
["PQSCr","Wp Net",20460,2,"4","Float IEE754","Word 0","kWh","Absolute Active Power Hours"]
["PQSCr","Wq Net",20462,2,"4","Float IEE754","Word 0","kVArh","Absolute Reactive Power Hours"]
["PQSCr","Ws Net",20464,2,"4","Float IEE754","Word 0","kVAh","Absolute Apparent Power Hours"]
["PQSCr","P 1",20496,2,"4","Float IEE754","Word 0","W","Measured value (calculated): Active power in positive sequence system (P- = Fed Active Power, P+ = Consumpted Active Power). This can be used to monitor the maximum power infeed/consumption."]
["PQSCr","Q 1",20498,2,"4","Float IEE754","Word 0","VAr","Measured value (calculated): Reactive power in positive sequence system (Q- = Fed Reactive Power, Q+ = Consumpted Reactive Power)"]
["PQSCr","cos phi max",21092,2,"4","Float IEE754","Word 0","-","Maximum value of the power factor: Sign Convention: sign(PF) = sign(P )"]
["PQSCr","cos phi min",21094,2,"4","Float IEE754","Word 0","-","Minimum value of the power factor: Sign Convention: sign(PF) = sign(P )"]
["PQSCr","P avg",21556,2,"4","Float IEE754","Word 0","W","Average of the active power"]
["PQSCr","P max",21558,2,"4","Float IEE754","Word 0","W","Maximum value of the active power"]
["PQSCr","P min",21560,2,"4","Float IEE754","Word 0","W","Minimum value of the active power"]
["PQSCr","S avg (Demand)",21562,2,"4","Float IEE754","Word 0","VA","Average of the apparent power"]
["PQSCr","S max",21564,2,"4","Float IEE754","Word 0","VA","Maximum value of the apparent power"]
["PQSCr","S min",21566,2,"4","Float IEE754","Word 0","VA","Minimum value of the apparent power"]
["PQSCr","cos phi max RMS",21570,2,"4","Float IEE754","Word 0","-","Maximum value of the power factor: Sign Convention: sign(PF) = sign(P )"]
["PQSCr","cos phi min RMS",21572,2,"4","Float IEE754","Word 0","-","Minimum value of the power factor: Sign Convention: sign(PF) = sign(P )"]
["PQSCr","Q avg (Demand)",21574,2,"4","Float IEE754","Word 0","VAr","Average of the reactive power"]
["PQSCr","Q max",21576,2,"4","Float IEE754","Word 0","VAr","Maximum value of the reactive power"]
["PQSCr","Q min",21578,2,"4","Float IEE754","Word 0","VAr","Minimum value of the reactive power"]
["PQSCr","Watt Peak (Demand)",21790,2,"4","Float IEE754","Word 0","W","WATTS Peak value, RMS value"]
["PQSCr","VAr Peak (Demand)",21792,2,"4","Float IEE754","Word 0","VAr","VARs Peak value, RMS value"]
["PQSCr","VA Peak (Demand)",21794,2,"4","Float IEE754","Word 0","VA","VA Peak value, RMS value"]
["PQSCr - fault value","cos phi ",50152,2,"4","Float IEE754","Word 0","-","Measured value (calculated): Power factor: Sign Convention: sign(PF) = sign(P ) , as stored in the Fault Recorder"]
["PQSCr - fault value","P  ",50154,2,"4","Float IEE754","Word 0","W","Measured value (calculated): Active power (P- = Fed Active Power, P+ = Consumpted Active Power) (fundamental) , as stored in the Fault Recorder"]
["PQSCr - fault value","Q  ",50156,2,"4","Float IEE754","Word 0","VAr","Measured value (calculated): Reactive power (Q- = Fed Reactive Power, Q+ = Consumpted Reactive Power) (fundamental) , as stored in the Fault Recorder"]
["PQSCr - fault value","S  ",50158,2,"4","Float IEE754","Word 0","VA","Measured Value (Calculated): Apparent power (fundamental) , as stored in the Fault Recorder"]
["PQSCr - fault value","P  RMS",50452,2,"4","Float IEE754","Word 0","W","Measured value (calculated): Active power (P- = Fed Active Power, P+ = Consumpted Active Power) (RMS) , as stored in the Fault Recorder"]
["PQSCr - fault value","S  RMS",50454,2,"4","Float IEE754","Word 0","VA","Measured Value (Calculated): Apparent power (RMS) , as stored in the Fault Recorder"]
["PQSCr - fault value","cos phi RMS",50456,2,"4","Float IEE754","Word 0","-","Measured value (calculated): Power factor: Sign Convention: sign(PF) = sign(P ) , as stored in the Fault Recorder"]
["PQSCr - fault value","P 1",50496,2,"4","Float IEE754","Word 0","W","Measured value (calculated): Active power in positive sequence system (P- = Fed Active Power, P+ = Consumpted Active Power). This can be used to monitor the maximum power infeed/consumption. , as stored in the Fault Recorder"]
["PQSCr - fault value","Q 1",50498,2,"4","Float IEE754","Word 0","VAr","Measured value (calculated): Reactive power in positive sequence system (Q- = Fed Reactive Power, Q+ = Consumpted Reactive Power) , as stored in the Fault Recorder"]
["PQS[1]","NumberOfAlarms",20582,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["PQS[1]","NumberOfTripCmds",20584,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["PQS[2]","NumberOfAlarms",20586,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["PQS[2]","NumberOfTripCmds",20588,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["PQS[3]","NumberOfAlarms",20590,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["PQS[3]","NumberOfTripCmds",20592,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["PQS[4]","NumberOfAlarms",20594,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["PQS[4]","NumberOfTripCmds",20596,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["PQS[5]","NumberOfAlarms",20598,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["PQS[5]","NumberOfTripCmds",20600,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["PQS[6]","NumberOfAlarms",20602,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["PQS[6]","NumberOfTripCmds",20604,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["RTD","HottestWindingTemp",20504,2,"4","Float IEE754","Word 0","°C","The actual value for the hottest winding temperature."]
["RTD","Hottest MotBearTemp",20506,2,"4","Float IEE754","Word 0","°C","The actual value for the hottest motor bearing temperature. "]
["RTD","Hottest LoadBearTemp",20508,2,"4","Float IEE754","Word 0","°C","The actual value for the hottest load bearing temperature."]
["RTD","HighestLbTemp",21618,2,"4","Float IEE754","Word 0","°C","Highest load bearing temperature since the last reset. Resettable via »Sys . Res OperationsCr« oder »Sys . Res All«."]
["RTD","HighestMbTemp",21620,2,"4","Float IEE754","Word 0","°C","Highest motor bearing temperature since the last reset. Resettable via »Sys . Res OperationsCr« oder »Sys . Res All«."]
["RTD","HighestWdTemp",21622,2,"4","Float IEE754","Word 0","°C","Highest motor winding temperature since the last reset. Resettable via »Sys . Res OperationsCr« oder »Sys . Res All«."]
["RTD","nAuxAlarms",21624,2,"4","Float IEE754","Word 0","-","Number of auxiliary temperature alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["RTD","nAuxTrips",21626,2,"4","Float IEE754","Word 0","-","Number of auxiliary temperature trips since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["RTD","nChannelFails",21628,2,"4","Float IEE754","Word 0","-","Number of RTD channel failures. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["RTD","nLbAlarms",21630,2,"4","Float IEE754","Word 0","-","Number of load bearing temperature alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["RTD","nLbTrips",21632,2,"4","Float IEE754","Word 0","-","Number of load bearing temperature trips since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["RTD","nMbAlarms",21634,2,"4","Float IEE754","Word 0","-","Number of motor bearing temperature alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["RTD","nMbTrips",21636,2,"4","Float IEE754","Word 0","-","Number of motor bearing temperature trips since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["RTD","nWdAlarms",21638,2,"4","Float IEE754","Word 0","-","Number of winding temperature alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["RTD","nWdTrips",21640,2,"4","Float IEE754","Word 0","-","Number of winding temperature trips since last reset. Resettable with »Sys . Res TripCr« or »Sys . Res All«."]
["RTD","Hottest Aux Temp",21820,2,"4","Float IEE754","Word 0","°C","The actual value for the hottest Auxiliary temperature."]
["RTD","HighestAuxTemp",21822,2,"4","Float IEE754","Word 0","°C","Highest Auxiliary temperature since the last reset. Resettable via »Sys . Res OperationsCr« oder »Sys . Res All«."]
["SG[1]","TripCmd Cr",20006,2,"4","Float IEE754","Word 0","-","Counter: Total number of trips of the switchgear."]
["SG[1]","Sum trip IL1",20182,2,"4","Float IEE754","Word 0","A","Summation of the tripping currents phase"]
["SG[1]","Sum trip IL2",20184,2,"4","Float IEE754","Word 0","A","Summation of the tripping currents phase"]
["SG[1]","Sum trip IL3",20186,2,"4","Float IEE754","Word 0","A","Summation of the tripping currents phase"]
["SG[1]","Bkr Wear Level",20516,2,"4","Float IEE754","Word 0","%","Wear level of the circuit breaker. (100% means that the circuit breaker has to be maintained.)"]
["SG[1]","Isum Intr per hour",20518,2,"4","Float IEE754","Word 0","kA","Sum per hour of interrupting currents."]
["ThR","I2T Used",20482,2,"4","Float IEE754","Word 0","%","Thermal capacity used. "]
["ThR","I2T Remained",20484,2,"4","Float IEE754","Word 0","%","Thermal capacity remained. "]
["ThR","nAlarms",21658,2,"4","Float IEE754","Word 0","-","Number of alarms since the last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["ThR","NumberOfTripCmds",21660,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["ThR - fault value","I2T Used",50482,2,"4","Float IEE754","Word 0","%","Thermal capacity used.  , as stored in the Fault Recorder"]
["URTD","Aux2",20328,2,"4","Float IEE754","Word 0","°C","Auxiliary2"]
["URTD","Windg1",20330,2,"4","Float IEE754","Word 0","°C","Winding 1"]
["URTD","Windg2",20332,2,"4","Float IEE754","Word 0","°C","Winding 2"]
["URTD","Windg3",20334,2,"4","Float IEE754","Word 0","°C","Winding 3"]
["URTD","Windg4",20336,2,"4","Float IEE754","Word 0","°C","Winding 4"]
["URTD","Windg5",20338,2,"4","Float IEE754","Word 0","°C","Winding 5"]
["URTD","Windg6",20340,2,"4","Float IEE754","Word 0","°C","Winding 6"]
["URTD","MotBear1",20342,2,"4","Float IEE754","Word 0","°C","Motor Bearing 1"]
["URTD","MotBear2",20344,2,"4","Float IEE754","Word 0","°C","Motor Bearing 2"]
["URTD","LoadBear1",20346,2,"4","Float IEE754","Word 0","°C","Load Bearing 1"]
["URTD","LoadBear2",20348,2,"4","Float IEE754","Word 0","°C","Load Bearing 2"]
["URTD","Aux1",20350,2,"4","Float IEE754","Word 0","°C","Auxiliary1"]
["URTD","RTD Max",20486,2,"4","Float IEE754","Word 0","°C","Maximum temperature of all channels."]
["URTD","Windg1 max",21194,2,"4","Float IEE754","Word 0","°C","Winding1 Maximum Value"]
["URTD","Windg2 max",21196,2,"4","Float IEE754","Word 0","°C","Winding2 Maximum Value"]
["URTD","Windg3 max",21198,2,"4","Float IEE754","Word 0","°C","Winding3 Maximum Value"]
["URTD","Windg4 max",21200,2,"4","Float IEE754","Word 0","°C","Winding4 Maximum Value"]
["URTD","Windg5 max",21202,2,"4","Float IEE754","Word 0","°C","Winding5 Maximum Value"]
["URTD","Windg6 max",21204,2,"4","Float IEE754","Word 0","°C","Winding6 Maximum Value"]
["URTD","MotBear1 max",21206,2,"4","Float IEE754","Word 0","°C","Motor Bearing1 Maximum Value"]
["URTD","MotBear2 max",21208,2,"4","Float IEE754","Word 0","°C","Motor Bearing2 Maximum Value"]
["URTD","LoadBear1 max",21210,2,"4","Float IEE754","Word 0","°C","Load Bearing1 Maximum Value"]
["URTD","LoadBear2 max",21212,2,"4","Float IEE754","Word 0","°C","Load Bearing2 Maximum Value"]
["URTD","Aux1 max",21214,2,"4","Float IEE754","Word 0","°C","Auxiliary1 Maximum Value"]
["URTD","Aux2 max",21800,2,"4","Float IEE754","Word 0","°C","Auxiliary2 Maximum Value"]
["URTD - fault value","Aux2",50328,2,"4","Float IEE754","Word 0","°C","Auxiliary2 , as stored in the Fault Recorder"]
["URTD - fault value","Windg1",50330,2,"4","Float IEE754","Word 0","°C","Winding 1 , as stored in the Fault Recorder"]
["URTD - fault value","Windg2",50332,2,"4","Float IEE754","Word 0","°C","Winding 2 , as stored in the Fault Recorder"]
["URTD - fault value","Windg3",50334,2,"4","Float IEE754","Word 0","°C","Winding 3 , as stored in the Fault Recorder"]
["URTD - fault value","Windg4",50336,2,"4","Float IEE754","Word 0","°C","Winding 4 , as stored in the Fault Recorder"]
["URTD - fault value","Windg5",50338,2,"4","Float IEE754","Word 0","°C","Winding 5 , as stored in the Fault Recorder"]
["URTD - fault value","Windg6",50340,2,"4","Float IEE754","Word 0","°C","Winding 6 , as stored in the Fault Recorder"]
["URTD - fault value","MotBear1",50342,2,"4","Float IEE754","Word 0","°C","Motor Bearing 1 , as stored in the Fault Recorder"]
["URTD - fault value","MotBear2",50344,2,"4","Float IEE754","Word 0","°C","Motor Bearing 2 , as stored in the Fault Recorder"]
["URTD - fault value","LoadBear1",50346,2,"4","Float IEE754","Word 0","°C","Load Bearing 1 , as stored in the Fault Recorder"]
["URTD - fault value","LoadBear2",50348,2,"4","Float IEE754","Word 0","°C","Load Bearing 2 , as stored in the Fault Recorder"]
["URTD - fault value","Aux1",50350,2,"4","Float IEE754","Word 0","°C","Auxiliary1 , as stored in the Fault Recorder"]
["V012[1]","NumberOfTripCmds",21886,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V012[1]","NumberOfAlarms",21888,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V012[2]","NumberOfTripCmds",21890,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V012[2]","NumberOfAlarms",21892,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V012[3]","NumberOfAlarms",21914,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V012[3]","NumberOfTripCmds",21916,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V012[4]","NumberOfAlarms",21918,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V012[4]","NumberOfTripCmds",21920,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V012[5]","NumberOfAlarms",21922,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V012[5]","NumberOfTripCmds",21924,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V012[6]","NumberOfAlarms",21926,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V012[6]","NumberOfTripCmds",21928,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["VG[1]","NumberOfTripCmds",21854,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["VG[1]","NumberOfAlarms",21856,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["VG[2]","NumberOfTripCmds",21858,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["VG[2]","NumberOfAlarms",21860,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["VT","f",20128,2,"4","Float IEE754","Word 0","Hz","Measured value: Frequency"]
["VT","VL12 ",20130,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (fundamental)"]
["VT","VL23 ",20132,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (fundamental)"]
["VT","VL31 ",20134,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (fundamental)"]
["VT","VL1 ",20136,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (fundamental)"]
["VT","VL2 ",20138,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (fundamental)"]
["VT","VL3 ",20140,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (fundamental)"]
["VT","VX meas ",20142,2,"4","Float IEE754","Word 0","V","Measured value (measured): VX measured (fundamental)"]
["VT","V0 ",20146,2,"4","Float IEE754","Word 0","V","Measured value (calculated): Symmetrical components Zero voltage(fundamental)"]
["VT","V1 ",20148,2,"4","Float IEE754","Word 0","V","Measured value (calculated): Symmetrical components positive phase sequence voltage(fundamental)"]
["VT","V2 ",20150,2,"4","Float IEE754","Word 0","V","Measured value (calculated): Symmetrical components negative phase sequence voltage(fundamental)"]
["VT","VG calc ",20162,2,"4","Float IEE754","Word 0","V","Measured value (calculated): VG (fundamental)"]
["VT","phi VG calc",20386,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VG calc\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi VX meas",20388,2,"4","Float IEE754","Word 0","°","Measured value: Angle of Phasor VX meas\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi VL12",20390,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL12\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi VL1",20392,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL1\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi VL23",20394,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL23\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi VL2",20396,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL2\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi VL31",20398,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL31\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi VL3",20400,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL3\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi V0",20402,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle Zero Sequence System\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi V1",20404,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Positive Sequence System\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","phi V2",20406,2,"4","Float IEE754","Word 0","°","Measured Value (calculated): Angle of Negative Sequence System\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude."]
["VT","VL1  THD",20408,2,"4","Float IEE754","Word 0","V","Measured value (calculated): VL1 Total Harmonic Distortion "]
["VT","VL12 THD",20410,2,"4","Float IEE754","Word 0","V","Measured value (calculated): V12 Total Harmonic Distortion "]
["VT","VL2 THD",20412,2,"4","Float IEE754","Word 0","V","Measured value (calculated): VL2 Total Harmonic Distortion "]
["VT","VL23 THD",20414,2,"4","Float IEE754","Word 0","V","Measured value (calculated): V23 Total Harmonic Distortion "]
["VT","VL3 THD",20416,2,"4","Float IEE754","Word 0","V","Measured value (calculated): VL3 Total Harmonic Distortion "]
["VT","VL31 THD",20418,2,"4","Float IEE754","Word 0","V","Measured value (calculated): V31 Total Harmonic Distortion "]
["VT","%VL1  THD",20420,2,"4","Float IEE754","Word 0","%","Measured value (calculated): VL1 Total Harmonic Distortion / Ground wave "]
["VT","%VL12 THD",20422,2,"4","Float IEE754","Word 0","%","Measured value (calculated): V12 Total Harmonic Distortion / Ground wave "]
["VT","%VL2 THD",20424,2,"4","Float IEE754","Word 0","%","Measured value (calculated): VL2 Total Harmonic Distortion / Ground wave "]
["VT","%VL23 THD",20426,2,"4","Float IEE754","Word 0","%","Measured value (calculated): V23 Total Harmonic Distortion / Ground wave "]
["VT","%VL3 THD",20428,2,"4","Float IEE754","Word 0","%","Measured value (calculated): VL3 Total Harmonic Distortion / Ground wave "]
["VT","%VL31 THD",20430,2,"4","Float IEE754","Word 0","%","Measured value (calculated): V31 Total Harmonic Distortion / Ground wave "]
["VT","VG calc RMS",20432,2,"4","Float IEE754","Word 0","V","Measured value (calculated): VG (RMS)"]
["VT","VX meas RMS",20434,2,"4","Float IEE754","Word 0","V","Measured value (measured): VX measured (RMS)"]
["VT","VL1 RMS",20436,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (RMS)"]
["VT","VL12 RMS",20438,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (RMS)"]
["VT","VL2 RMS",20440,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (RMS)"]
["VT","VL23 RMS",20442,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (RMS)"]
["VT","VL3 RMS",20444,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (RMS)"]
["VT","VL31 RMS",20446,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (RMS)"]
["VT","%(V2/V1)",20450,2,"4","Float IEE754","Word 0","%","Measured value (calculated): V2/V1, phase sequence will be taken into account automatically."]
["VT","V/f",20646,2,"4","Float IEE754","Word 0","%","Ratio Volts/Hertz  in relation to nominal values."]
["VT","f max",21002,2,"4","Float IEE754","Word 0","Hz","Max. frequency value"]
["VT","f min ",21004,2,"4","Float IEE754","Word 0","Hz","Min. frequency value"]
["VT","V1 max ",21044,2,"4","Float IEE754","Word 0","V","Maximum value: Symmetrical components positive phase sequence voltage(fundamental)"]
["VT","V1 min ",21046,2,"4","Float IEE754","Word 0","V","Minimum value: Symmetrical components positive phase sequence voltage(fundamental)"]
["VT","V2 max ",21050,2,"4","Float IEE754","Word 0","V","Maximum value: Symmetrical components negative phase sequence voltage(fundamental)"]
["VT","V2 min ",21052,2,"4","Float IEE754","Word 0","V","Minimum value: Symmetrical components negative phase sequence voltage(fundamental)"]
["VT","delta phi",21126,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Vector surge"]
["VT","df/dt",21128,2,"4","Float IEE754","Word 0","Hz/s","Measured value (calculated): Rate-of-frequency-change."]
["VT","VG calc max RMS",21498,2,"4","Float IEE754","Word 0","V","Measured value (calculated):VX maximum value (RMS)"]
["VT","VG calc min  RMS",21500,2,"4","Float IEE754","Word 0","V","Measured value (calculated):VX minimum value  (RMS)"]
["VT","VX meas max RMS",21504,2,"4","Float IEE754","Word 0","V","Measured value: VX maximum value (RMS)"]
["VT","VX meas min  RMS",21506,2,"4","Float IEE754","Word 0","V","Measured value: VX minimum value  (RMS)"]
["VT","VL12 max RMS",21510,2,"4","Float IEE754","Word 0","V","VL12 maximum value (RMS)"]
["VT","VL12 min  RMS",21512,2,"4","Float IEE754","Word 0","V","VL12 minimum value  (RMS)"]
["VT","VL1 max RMS",21516,2,"4","Float IEE754","Word 0","V","VL1 maximum value (RMS)"]
["VT","VL1 min  RMS",21518,2,"4","Float IEE754","Word 0","V","VL1 minimum value  (RMS)"]
["VT","VL23 max RMS",21522,2,"4","Float IEE754","Word 0","V","VL23 maximum value (RMS)"]
["VT","VL23 min  RMS",21524,2,"4","Float IEE754","Word 0","V","VL23 minimum value  (RMS)"]
["VT","VL2 max RMS",21528,2,"4","Float IEE754","Word 0","V","VL2 maximum value (RMS)"]
["VT","VL2 min  RMS",21530,2,"4","Float IEE754","Word 0","V","VL2 minimum value  (RMS)"]
["VT","VL31 max RMS",21534,2,"4","Float IEE754","Word 0","V","VL31 maximum value (RMS)"]
["VT","VL31 min  RMS",21536,2,"4","Float IEE754","Word 0","V","VL31 minimum value  (RMS)"]
["VT","VL3 max RMS",21540,2,"4","Float IEE754","Word 0","V","VL3 maximum value (RMS)"]
["VT","VL3 min  RMS",21542,2,"4","Float IEE754","Word 0","V","VL3 minimum value  (RMS)"]
["VT","%(V2/V1) max",21552,2,"4","Float IEE754","Word 0","%","Measured value (calculated):V2/V1 maximum value, phase sequence will be taken into account automatically"]
["VT","%(V2/V1) min",21554,2,"4","Float IEE754","Word 0","%","Measured value (calculated):V2/V1 minimum value , phase sequence will be taken into account automatically"]
["VT","V/f max",21894,2,"4","Float IEE754","Word 0","%","Maximum value: Ratio Volts/Hertz in relation to nominal values."]
["VT","V/f min",21896,2,"4","Float IEE754","Word 0","%","Minimum value: Ratio Volts/Hertz  in relation to nominal values."]
["VT - fault value","f",50128,2,"4","Float IEE754","Word 0","Hz","Measured value: Frequency , as stored in the Fault Recorder"]
["VT - fault value","VL12 ",50130,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (fundamental) , as stored in the Fault Recorder"]
["VT - fault value","VL23 ",50132,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (fundamental) , as stored in the Fault Recorder"]
["VT - fault value","VL31 ",50134,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (fundamental) , as stored in the Fault Recorder"]
["VT - fault value","VL1 ",50136,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (fundamental) , as stored in the Fault Recorder"]
["VT - fault value","VL2 ",50138,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (fundamental) , as stored in the Fault Recorder"]
["VT - fault value","VL3 ",50140,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (fundamental) , as stored in the Fault Recorder"]
["VT - fault value","VX meas ",50142,2,"4","Float IEE754","Word 0","V","Measured value (measured): VX measured (fundamental) , as stored in the Fault Recorder"]
["VT - fault value","V0 ",50146,2,"4","Float IEE754","Word 0","V","Measured value (calculated): Symmetrical components Zero voltage(fundamental) , as stored in the Fault Recorder"]
["VT - fault value","V1 ",50148,2,"4","Float IEE754","Word 0","V","Measured value (calculated): Symmetrical components positive phase sequence voltage(fundamental) , as stored in the Fault Recorder"]
["VT - fault value","V2 ",50150,2,"4","Float IEE754","Word 0","V","Measured value (calculated): Symmetrical components negative phase sequence voltage(fundamental) , as stored in the Fault Recorder"]
["VT - fault value","VG calc ",50162,2,"4","Float IEE754","Word 0","V","Measured value (calculated): VG (fundamental) , as stored in the Fault Recorder"]
["VT - fault value","phi VG calc",50386,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VG calc\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["VT - fault value","phi VX meas",50388,2,"4","Float IEE754","Word 0","°","Measured value: Angle of Phasor VX meas\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["VT - fault value","phi VL12",50390,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL12\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["VT - fault value","phi VL1",50392,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL1\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["VT - fault value","phi VL23",50394,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL23\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["VT - fault value","phi VL2",50396,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL2\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["VT - fault value","phi VL31",50398,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL31\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["VT - fault value","phi VL3",50400,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Angle of Phasor VL3\\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder"]
["VT - fault value","VG calc RMS",50432,2,"4","Float IEE754","Word 0","V","Measured value (calculated): VG (RMS) , as stored in the Fault Recorder"]
["VT - fault value","VX meas RMS",50434,2,"4","Float IEE754","Word 0","V","Measured value (measured): VX measured (RMS) , as stored in the Fault Recorder"]
["VT - fault value","VL1 RMS",50436,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (RMS) , as stored in the Fault Recorder"]
["VT - fault value","VL12 RMS",50438,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (RMS) , as stored in the Fault Recorder"]
["VT - fault value","VL2 RMS",50440,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (RMS) , as stored in the Fault Recorder"]
["VT - fault value","VL23 RMS",50442,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (RMS) , as stored in the Fault Recorder"]
["VT - fault value","VL3 RMS",50444,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-neutral voltage (RMS) , as stored in the Fault Recorder"]
["VT - fault value","VL31 RMS",50446,2,"4","Float IEE754","Word 0","V","Measured value: Phase-to-phase voltage (RMS) , as stored in the Fault Recorder"]
["VT - fault value","delta phi",51126,2,"4","Float IEE754","Word 0","°","Measured value (calculated): Vector surge , as stored in the Fault Recorder"]
["VT - fault value","df/dt",51128,2,"4","Float IEE754","Word 0","Hz/s","Measured value (calculated): Rate-of-frequency-change. , as stored in the Fault Recorder"]
["V[1]","NumberOfAlarms",21830,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V[1]","NumberOfTripCmds",21832,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V[2]","NumberOfAlarms",21834,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V[2]","NumberOfTripCmds",21836,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V[3]","NumberOfAlarms",21838,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V[3]","NumberOfTripCmds",21840,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V[4]","NumberOfAlarms",21842,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V[4]","NumberOfTripCmds",21844,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V[5]","NumberOfAlarms",21846,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V[5]","NumberOfTripCmds",21848,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["V[6]","NumberOfAlarms",21850,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["V[6]","NumberOfTripCmds",21852,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["Values","Build",20008,2,"4","Float IEE754","Word 0","-","Build Number"]
["Values","Operating hours Cr",20010,2,"4","Float IEE754","Word 0","h","Operating hours counter of the protective device"]
["Values","Hours Counter",20514,2,"4","Float IEE754","Word 0","h","Resettable device operation hours counter. Resettable with »Sys . Res TotalCr« or »Sys . Res All«."]
["f[1]","NumberOfTripCmds",21862,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["f[1]","NumberOfAlarms",21864,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["f[2]","NumberOfTripCmds",21866,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["f[2]","NumberOfAlarms",21868,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["f[3]","NumberOfTripCmds",21870,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["f[3]","NumberOfAlarms",21872,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["f[4]","NumberOfTripCmds",21874,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["f[4]","NumberOfAlarms",21876,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["f[5]","NumberOfTripCmds",21878,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["f[5]","NumberOfAlarms",21880,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]
["f[6]","NumberOfTripCmds",21882,2,"4","Float IEE754","Word 0","-","Number of trip commands since the last reset"]
["f[6]","NumberOfAlarms",21884,2,"4","Float IEE754","Word 0","-","Number of alarms since last reset. Resettable with »Sys . Res AlarmCr« or »Sys . Res All«."]

{"sheet":"causeOfTrip","index":5,"n_rows":53,"n_cols":3,"rows_kept":53,"cut":false,"hidden":false,"merged":[]}
["COT modules","COT Code","COT description"]
[null,1,"NORM"]
["IG[1]",1201]
["IG[2]",1202]
["IG[3]",1203]
["IG[4]",1204]
["ExP[1]",1306]
["ExP[2]",1307]
["ExP[3]",1308]
["ExP[4]",1309]
["f[1]",1401]
["f[2]",1402]
["f[3]",1403]
["f[4]",1404]
["f[5]",1405]
["f[6]",1406]
["Jam[1]",2101]
["Jam[2]",2102]
["I2>[1]",2901]
["I2>[2]",2902]
["V012[1]",3001]
["V012[2]",3002]
["V012[3]",3003]
["V012[4]",3004]
["V012[5]",3005]
["V012[6]",3006]
["I[1]",3201]
["I[2]",3202]
["I[3]",3203]
["I[4]",3204]
["I[5]",3205]
["I[6]",3206]
["PQS[1]",3401]
["PQS[2]",3402]
["PQS[3]",3403]
["PQS[4]",3404]
["PQS[5]",3405]
["PQS[6]",3406]
["PF[1]",3501]
["PF[2]",3502]
["ThR",3701]
["I<[1]",3901]
["I<[2]",3902]
["I<[3]",3903]
["VG[1]",4001]
["VG[2]",4002]
["V[1]",4101]
["V[2]",4102]
["V[3]",4103]
["V[4]",4104]
["V[5]",4105]
["V[6]",4106]
["RTD",4201]