{"text_format":"2","workbook":"xlsx","n_sheets":6,"sheets":["Version","State","Adjust","Command","Measure","causeOfTrip"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Version","index":0,"n_rows":2,"n_cols":2,"rows_kept":2,"cut":false,"hidden":false,"merged":[]}
["Handoff","SW-Version"]
[61788,"3.10.a"]

{"sheet":"State","index":1,"n_rows":1663,"n_cols":9,"rows_kept":1663,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["AKÜ","ExBlo1-E",150,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["AKÜ","ExBlo2-E",150,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["AKÜ","Aktiv",150,1,"3","Bit","0x4","-","Meldung: aktiv"]
["AKÜ","ExBlo",150,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["AKÜ","Alarm",150,1,"3","Bit","0x10","-","Meldung: Alarm Auslösekreisüberwachung"]
["AKÜ","nicht mögl",150,1,"3","Bit","0x20","-","Nicht möglich, weil kein Statusindikator rangiert wurde."]
["AKÜ","Hiko EIN-E",150,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52a)"]
["AKÜ","Hiko AUS-E",150,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52b)"]
["AWE","Aktiv",46,1,"3","Bit","0x1","-","Meldung: aktiv"]
["AWE","ExBlo",46,1,"3","Bit","0x2","-","Meldung: Externe Blockade"]
["AWE","läuft",46,1,"3","Bit","0x8","-","Meldung: Automatische Wiedereinschaltung läuft"]
["AWE","t-Pause",46,1,"3","Bit","0x10","-","Meldung: Pausenzeit zwischen Schutzauslösung und Wiedereinschaltversuch"]
["AWE","erfolgr (*)",46,1,"3","Bit","0x100","-","Meldung: Automatische Wiedereinschaltung war erfolgreich"]
["AWE","fehlgeschl (*)",46,1,"3","Bit","0x200","-","Meldung: Automatische Wiedereinschaltung fehlgeschlagen"]
["AWE","t-AWE Überwachung",46,1,"3","Bit","0x1000","-","Meldung:  AWE Überwachung "]
["AWE","ExBlo1-E",47,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["AWE","ExBlo2-E",47,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["AWE","LS EIN Bef",47,1,"3","Bit","0x10","-","Meldung: Einschaltbefehl an den Leistungsschalter"]
["AWE","Vorab Schuss (*)",47,1,"3","Bit","0x20","-","Steuerung des Vorab-Schusses"]
["AWE","Schuss 1 (*)",47,1,"3","Bit","0x40","-","Schusssteuerung"]
["AWE","Schuss 2 (*)",47,1,"3","Bit","0x80","-","Schusssteuerung"]
["AWE","Schuss 3 (*)",47,1,"3","Bit","0x100","-","Schusssteuerung"]
["AWE","Schuss 4 (*)",47,1,"3","Bit","0x200","-","Schusssteuerung"]
["AWE","Schuss 5 (*)",47,1,"3","Bit","0x400","-","Schusssteuerung"]
["AWE","Schuss 6 (*)",47,1,"3","Bit","0x800","-","Schusssteuerung"]
["AWE","Ex Verrieg-E",156,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Verriegelung der AWE."]
["AWE","Ex Schuss Ink-E",156,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Der AWE Zähler wird durch dieses externe Signal inkrementiert. Diese Funktionalität kann für die Zonenkoordination von vorgelagerten (upstream) Schutzgeräten, die ebenfalls über eine AWE-Funktionalität verfügen, verwendet werden. Achtung dieser Parameter gibt die Funktionalität nur grundsätzlich frei. Die eigentliche Rangierung muss in den Globalen Parametern vorgenommen werden."]
["AWE","Blo",156,1,"3","Bit","0x4","-","Meldung: AWE blockiert"]
["AWE","t-Blo nach LS man EIN",156,1,"3","Bit","0x8","-","Meldung: Blockade nach manueller Einschaltung des Leistungsschalters. Dieser Timer wird gestartet, wenn der Leistungsschalter manuell eingeschaltet wurde. Während dieser Timer läuft ist kein AWE Start möglich."]
["AWE","Verr",156,1,"3","Bit","0x10","-","Meldung: AWE verriegelt"]
["AWE","t-Reset Verrieg",156,1,"3","Bit","0x20","-","Meldung:  Verzögerungs-Timer für das Zurücksetzen der AWE Verriegelung. Nachdem vom Gerät das Rücksetzsignal (z.B. über einen digitalen Eingang oder Scada) erkannt wurde, wird das Zurücksetzen der AWE um diese Zeit verzögert."]
["AWE","wiedereinschaltbereit",156,1,"3","Bit","0x40","-","Meldung: Wiedereinschaltbereit"]
["AWE","t-Run2Ready",156,1,"3","Bit","0x80","-","Meldung:  Untersuchungszeit: Wenn der Leistungsschalter nach einem Wiedereinschaltversuch für die Dauer dieser Zeit eingeschaltet bleibt, dann war die AWE erfolgreich und das AWE Modul kehrt in den Bereitschaftszustand zurück."]
["AWE","Bereitschaft",156,1,"3","Bit","0x100","-","Meldung: Allgemeine Bereitschaft"]
["AWE","Service Alarm 1",156,1,"3","Bit","0x200","-","Meldung: Service Alarm 1, zu viele Schaltspiele."]
["AWE","Service Alarm 2",156,1,"3","Bit","0x400","-","Meldung: AWE - Service Alarm 2,  zu viele Schaltspiele"]
["AWE","Max Schüsse / h überschr",156,1,"3","Bit","0x800","-","Meldung:  Die höchstzulässige Anzahl an Wiedereinschaltversuchen pro Stunde wurde überschritten."]
["AnEing[1]","Drahtbruch",247,1,"3","Bit","0x1","-","Meldung: Drahtbruch. Diese Meldung ist nur gültig, wenn der Analogeingang im Modus 4...20 mA betrieben wird."]
["AnEing[1]","Eing erzwungen",247,1,"3","Bit","0x2","-","Der Wert des Analogeingangs wurde erzwungen (gesetzt). Das bedeutet, dass der Wert des Analogeingangs nicht dem realen Messwert am Eingang entspricht."]
["AnEing[2]","Drahtbruch",248,1,"3","Bit","0x4","-","Meldung: Drahtbruch. Diese Meldung ist nur gültig, wenn der Analogeingang im Modus 4...20 mA betrieben wird."]
["AnEing[2]","Eing erzwungen",248,1,"3","Bit","0x8","-","Der Wert des Analogeingangs wurde erzwungen (gesetzt). Das bedeutet, dass der Wert des Analogeingangs nicht dem realen Messwert am Eingang entspricht."]
["AnaP[1]","ExBlo1-E",224,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["AnaP[1]","ExBlo2-E",224,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["AnaP[1]","ExBlo AuslBef-E",224,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["AnaP[1]","Aktiv",224,1,"3","Bit","0x8","-","Meldung: aktiv"]
["AnaP[1]","ExBlo",224,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["AnaP[1]","Blo AuslBef",224,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["AnaP[1]","ExBlo AuslBef",224,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["AnaP[1]","Anregung",224,1,"3","Bit","0x80","-","Meldung: Alarm Analogeingang"]
["AnaP[1]","Ausl (*)",224,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["AnaP[1]","AuslBef (*)",224,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["AnaP[2]","ExBlo1-E",225,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["AnaP[2]","ExBlo2-E",225,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["AnaP[2]","ExBlo AuslBef-E",225,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["AnaP[2]","Aktiv",225,1,"3","Bit","0x8","-","Meldung: aktiv"]
["AnaP[2]","ExBlo",225,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["AnaP[2]","Blo AuslBef",225,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["AnaP[2]","ExBlo AuslBef",225,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["AnaP[2]","Anregung",225,1,"3","Bit","0x80","-","Meldung: Alarm Analogeingang"]
["AnaP[2]","Ausl (*)",225,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["AnaP[2]","AuslBef (*)",225,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["AnaP[3]","ExBlo1-E",226,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["AnaP[3]","ExBlo2-E",226,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["AnaP[3]","ExBlo AuslBef-E",226,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["AnaP[3]","Aktiv",226,1,"3","Bit","0x8","-","Meldung: aktiv"]
["AnaP[3]","ExBlo",226,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["AnaP[3]","Blo AuslBef",226,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["AnaP[3]","ExBlo AuslBef",226,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["AnaP[3]","Anregung",226,1,"3","Bit","0x80","-","Meldung: Alarm Analogeingang"]
["AnaP[3]","Ausl (*)",226,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["AnaP[3]","AuslBef (*)",226,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["AnaP[4]","ExBlo1-E",227,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["AnaP[4]","ExBlo2-E",227,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["AnaP[4]","ExBlo AuslBef-E",227,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["AnaP[4]","Aktiv",227,1,"3","Bit","0x8","-","Meldung: aktiv"]
["AnaP[4]","ExBlo",227,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["AnaP[4]","Blo AuslBef",227,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["AnaP[4]","ExBlo AuslBef",227,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["AnaP[4]","Anregung",227,1,"3","Bit","0x80","-","Meldung: Alarm Analogeingang"]
["AnaP[4]","Ausl (*)",227,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["AnaP[4]","AuslBef (*)",227,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["DI Slot X1","DI 1",1000,1,"3","Bit","0x1","-","Meldung: Digitaler Eingang"]
["DI Slot X1","DI 2",1000,1,"3","Bit","0x2","-","Meldung: Digitaler Eingang"]
["DI Slot X1","DI 3",1000,1,"3","Bit","0x4","-","Meldung: Digitaler Eingang"]
["DI Slot X1","DI 4",1000,1,"3","Bit","0x8","-","Meldung: Digitaler Eingang"]
["DI Slot X1","DI 5",1000,1,"3","Bit","0x10","-","Meldung: Digitaler Eingang"]
["DI Slot X1","DI 6",1000,1,"3","Bit","0x20","-","Meldung: Digitaler Eingang"]
["DI Slot X1","DI 7",1000,1,"3","Bit","0x40","-","Meldung: Digitaler Eingang"]
["DI Slot X1","DI 8",1000,1,"3","Bit","0x80","-","Meldung: Digitaler Eingang"]
["DI Slot X5","DI 1",1014,1,"3","Bit","0x1","-","Meldung: Digitaler Eingang"]
["DI Slot X5","DI 2",1014,1,"3","Bit","0x2","-","Meldung: Digitaler Eingang"]
["DI Slot X5","DI 3",1014,1,"3","Bit","0x4","-","Meldung: Digitaler Eingang"]
["DI Slot X5","DI 4",1014,1,"3","Bit","0x8","-","Meldung: Digitaler Eingang"]
["DI Slot X5","DI 5",1014,1,"3","Bit","0x10","-","Meldung: Digitaler Eingang"]
["DI Slot X5","DI 6",1014,1,"3","Bit","0x20","-","Meldung: Digitaler Eingang"]
["DI Slot X5","DI 7",1014,1,"3","Bit","0x40","-","Meldung: Digitaler Eingang"]
["DI Slot X5","DI 8",1014,1,"3","Bit","0x80","-","Meldung: Digitaler Eingang"]
["DI Slot X6","DI 1",1001,1,"3","Bit","0x1","-","Meldung: Digitaler Eingang"]
["DI Slot X6","DI 2",1001,1,"3","Bit","0x2","-","Meldung: Digitaler Eingang"]
["DI Slot X6","DI 3",1001,1,"3","Bit","0x4","-","Meldung: Digitaler Eingang"]
["DI Slot X6","DI 4",1001,1,"3","Bit","0x8","-","Meldung: Digitaler Eingang"]
["DI Slot X6","DI 5",1001,1,"3","Bit","0x10","-","Meldung: Digitaler Eingang"]
["DI Slot X6","DI 6",1001,1,"3","Bit","0x20","-","Meldung: Digitaler Eingang"]
["DI Slot X6","DI 7",1001,1,"3","Bit","0x40","-","Meldung: Digitaler Eingang"]
["DI Slot X6","DI 8",1001,1,"3","Bit","0x80","-","Meldung: Digitaler Eingang"]
["ExS[1]","ExBlo1-E",49,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["ExS[1]","ExBlo2-E",49,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["ExS[1]","ExBlo AuslBef-E",49,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["ExS[1]","Alarm-E",49,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Alarm"]
["ExS[1]","Ausl-E",49,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Auslösebefehl"]
["ExS[1]","Aktiv",49,1,"3","Bit","0x20","-","Meldung: aktiv"]
["ExS[1]","ExBlo",49,1,"3","Bit","0x40","-","Meldung: Externe Blockade"]
["ExS[1]","Blo AuslBef",49,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["ExS[1]","ExBlo AuslBef",49,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["ExS[1]","Alarm",49,1,"3","Bit","0x200","-","Meldung: Alarm"]
["ExS[1]","Ausl (*)",49,1,"3","Bit","0x400","-","Meldung: Auslösung"]
["ExS[1]","AuslBef (*)",49,1,"3","Bit","0x800","-","Meldung: Auslösebefehl"]
["ExS[2]","ExBlo1-E",50,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["ExS[2]","ExBlo2-E",50,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["ExS[2]","ExBlo AuslBef-E",50,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["ExS[2]","Alarm-E",50,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Alarm"]
["ExS[2]","Ausl-E",50,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Auslösebefehl"]
["ExS[2]","Aktiv",50,1,"3","Bit","0x20","-","Meldung: aktiv"]
["ExS[2]","ExBlo",50,1,"3","Bit","0x40","-","Meldung: Externe Blockade"]
["ExS[2]","Blo AuslBef",50,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["ExS[2]","ExBlo AuslBef",50,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["ExS[2]","Alarm",50,1,"3","Bit","0x200","-","Meldung: Alarm"]
["ExS[2]","Ausl (*)",50,1,"3","Bit","0x400","-","Meldung: Auslösung"]
["ExS[2]","AuslBef (*)",50,1,"3","Bit","0x800","-","Meldung: Auslösebefehl"]
["ExS[3]","ExBlo1-E",51,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["ExS[3]","ExBlo2-E",51,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["ExS[3]","ExBlo AuslBef-E",51,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["ExS[3]","Alarm-E",51,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Alarm"]
["ExS[3]","Ausl-E",51,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Auslösebefehl"]
["ExS[3]","Aktiv",51,1,"3","Bit","0x20","-","Meldung: aktiv"]
["ExS[3]","ExBlo",51,1,"3","Bit","0x40","-","Meldung: Externe Blockade"]
["ExS[3]","Blo AuslBef",51,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["ExS[3]","ExBlo AuslBef",51,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["ExS[3]","Alarm",51,1,"3","Bit","0x200","-","Meldung: Alarm"]
["ExS[3]","Ausl (*)",51,1,"3","Bit","0x400","-","Meldung: Auslösung"]
["ExS[3]","AuslBef (*)",51,1,"3","Bit","0x800","-","Meldung: Auslösebefehl"]
["ExS[4]","ExBlo1-E",52,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["ExS[4]","ExBlo2-E",52,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["ExS[4]","ExBlo AuslBef-E",52,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["ExS[4]","Alarm-E",52,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Alarm"]
["ExS[4]","Ausl-E",52,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Auslösebefehl"]
["ExS[4]","Aktiv",52,1,"3","Bit","0x20","-","Meldung: aktiv"]
["ExS[4]","ExBlo",52,1,"3","Bit","0x40","-","Meldung: Externe Blockade"]
["ExS[4]","Blo AuslBef",52,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["ExS[4]","ExBlo AuslBef",52,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["ExS[4]","Alarm",52,1,"3","Bit","0x200","-","Meldung: Alarm"]
["ExS[4]","Ausl (*)",52,1,"3","Bit","0x400","-","Meldung: Auslösung"]
["ExS[4]","AuslBef (*)",52,1,"3","Bit","0x800","-","Meldung: Auslösebefehl"]
["FAS","ExBlo1-E",65,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["FAS","ExBlo2-E",65,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["FAS","Ext FAS-E",65,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externer Fehleraufschaltungsalarm"]
["FAS","Ex rückw Verr-E",65,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["FAS","Aktiv",65,1,"3","Bit","0x10","-","Meldung: aktiv"]
["FAS","ExBlo",65,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["FAS","Ex rückw Verr",65,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["FAS","AWE Blo",65,1,"3","Bit","0x400","-","Meldung: Blockade durch AWE "]
["FAS","freigegeben",65,1,"3","Bit","0x800","-","Meldung: Fehleraufschaltung freigegeben. Dieses Signal kann dazu benutzt werden um die Überstromzeitstufen zu beeinflussen."]
["FAS","I<",65,1,"3","Bit","0x2000","-","Meldung: Stromlos (Kein Laststrom)."]
["Fast Status","Gerätetyp",5000,1,"3","Bit","0xffff","-","Geräte-Typcode: Zeigt den Zusammenhang zwischen dem Gerätenamen und dem Modbus Code: \\nHighPROTEC: \\nMRI4 - 1000\\nMRU4 - 1001\\nMRA4 - 1002\\nMCA4 - 1003\\nMRDT4 - 1005\\nMCDTV4 - 1006\\nMCDGV4 - 1007\\nMRM4 - 1009\\nMRMV4 - 1010\\nMCDLV4 - 1011"]
["Fast Status","Komm Version",5001,1,"3","Bit","0xffff","-","Modbus Kommunikations-Versions-Nummer. Diese Versionsnummer wird geändert, wenn durch ein neues Modbus-Release Inkompabilitäten zwischen den Versionen entstehen sollten."]
["Fast Status","Konf Bin Eing1-E",5002,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing2-E",5002,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing3-E",5002,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing4-E",5002,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing5-E",5002,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing6-E",5002,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing7-E",5002,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing8-E",5002,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing9-E",5002,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing10-E",5002,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing11-E",5002,1,"3","Bit","0x400","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing12-E",5002,1,"3","Bit","0x800","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing13-E",5002,1,"3","Bit","0x1000","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing14-E",5002,1,"3","Bit","0x2000","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing15-E",5002,1,"3","Bit","0x4000","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing16-E",5002,1,"3","Bit","0x8000","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing17-E",5003,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing18-E",5003,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing19-E",5003,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing20-E",5003,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing21-E",5003,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing22-E",5003,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing23-E",5003,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing24-E",5003,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing25-E",5003,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing26-E",5003,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing27-E",5003,1,"3","Bit","0x400","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing28-E",5003,1,"3","Bit","0x800","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing29-E",5003,1,"3","Bit","0x1000","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing30-E",5003,1,"3","Bit","0x2000","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing31-E",5003,1,"3","Bit","0x4000","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Konf Bin Eing32-E",5003,1,"3","Bit","0x8000","-","Zustand des Moduleingangs: Konf Bin Eing"]
["Fast Status","Auslöseursache (*)",5004,1,"3","Bit","0xffff","-","Erste Auslöseursache. Diese wird als ganzzahliger Zahlenwert dargestellt und entspricht dem Namen des auslösenden Schutzmoduls im Fehlerrekorder. Die Zuordnung Zahlenwert-->Ursache lässt sich in der Tabelle „Grund der Auslösung“ in der SCADA-Dokumentation nachschlagen."]
["HVRT[1]","ExBlo1-E",298,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["HVRT[1]","ExBlo2-E",298,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["HVRT[1]","ExBlo AuslBef-E",298,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["HVRT[1]","Aktiv",298,1,"3","Bit","0x8","-","Meldung: aktiv"]
["HVRT[1]","ExBlo",298,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["HVRT[1]","Alarm",298,1,"3","Bit","0x20","-","Meldung: Alarm Spannungsstufe"]
["HVRT[1]","Alarm L1",298,1,"3","Bit","0x40","-","Meldung: Alarm L1"]
["HVRT[1]","Alarm L2",298,1,"3","Bit","0x80","-","Meldung: Alarm L2"]
["HVRT[1]","Alarm L3",298,1,"3","Bit","0x100","-","Meldung: Alarm L3"]
["HVRT[1]","Ausl (*)",298,1,"3","Bit","0x200","-","Meldung: Auslösung"]
["HVRT[1]","Ausl L1 (*)",298,1,"3","Bit","0x400","-","Meldung: General-Auslösung L1"]
["HVRT[1]","Ausl L2 (*)",298,1,"3","Bit","0x800","-","Meldung: General-Auslösung L2"]
["HVRT[1]","Ausl L3 (*)",298,1,"3","Bit","0x1000","-","Meldung: General-Auslösung L3"]
["HVRT[1]","AuslBef (*)",298,1,"3","Bit","0x2000","-","Meldung: Auslösebefehl"]
["HVRT[1]","Blo AuslBef",298,1,"3","Bit","0x4000","-","Meldung: Auslösebefehl blockiert"]
["HVRT[1]","ExBlo AuslBef",298,1,"3","Bit","0x8000","-","Meldung: Externe Blockade des Auslösekommandos"]
["HVRT[2]","ExBlo1-E",299,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["HVRT[2]","ExBlo2-E",299,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["HVRT[2]","ExBlo AuslBef-E",299,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["HVRT[2]","Aktiv",299,1,"3","Bit","0x8","-","Meldung: aktiv"]
["HVRT[2]","ExBlo",299,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["HVRT[2]","Alarm",299,1,"3","Bit","0x20","-","Meldung: Alarm Spannungsstufe"]
["HVRT[2]","Alarm L1",299,1,"3","Bit","0x40","-","Meldung: Alarm L1"]
["HVRT[2]","Alarm L2",299,1,"3","Bit","0x80","-","Meldung: Alarm L2"]
["HVRT[2]","Alarm L3",299,1,"3","Bit","0x100","-","Meldung: Alarm L3"]
["HVRT[2]","Ausl (*)",299,1,"3","Bit","0x200","-","Meldung: Auslösung"]
["HVRT[2]","Ausl L1 (*)",299,1,"3","Bit","0x400","-","Meldung: General-Auslösung L1"]
["HVRT[2]","Ausl L2 (*)",299,1,"3","Bit","0x800","-","Meldung: General-Auslösung L2"]
["HVRT[2]","Ausl L3 (*)",299,1,"3","Bit","0x1000","-","Meldung: General-Auslösung L3"]
["HVRT[2]","AuslBef (*)",299,1,"3","Bit","0x2000","-","Meldung: Auslösebefehl"]
["HVRT[2]","Blo AuslBef",299,1,"3","Bit","0x4000","-","Meldung: Auslösebefehl blockiert"]
["HVRT[2]","ExBlo AuslBef",299,1,"3","Bit","0x8000","-","Meldung: Externe Blockade des Auslösekommandos"]
["I2>[1]","ExBlo1-E",82,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["I2>[1]","ExBlo2-E",82,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["I2>[1]","ExBlo AuslBef-E",82,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["I2>[1]","Aktiv",82,1,"3","Bit","0x8","-","Meldung: aktiv"]
["I2>[1]","ExBlo",82,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["I2>[1]","Blo AuslBef",82,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["I2>[1]","ExBlo AuslBef",82,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["I2>[1]","Alarm",82,1,"3","Bit","0x80","-","Meldung: Alarm Asymmetrie"]
["I2>[1]","Ausl (*)",82,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["I2>[1]","AuslBef (*)",82,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["I2>[2]","ExBlo1-E",83,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["I2>[2]","ExBlo2-E",83,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["I2>[2]","ExBlo AuslBef-E",83,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["I2>[2]","Aktiv",83,1,"3","Bit","0x8","-","Meldung: aktiv"]
["I2>[2]","ExBlo",83,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["I2>[2]","Blo AuslBef",83,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["I2>[2]","ExBlo AuslBef",83,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["I2>[2]","Alarm",83,1,"3","Bit","0x80","-","Meldung: Alarm Asymmetrie"]
["I2>[2]","Ausl (*)",83,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["I2>[2]","AuslBef (*)",83,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["IE[1]","ExBlo1-E",15,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["IE[1]","ExBlo2-E",15,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["IE[1]","ExBlo AuslBef-E",15,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["IE[1]","Ex rückw Verr-E",15,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["IE[1]","Aktiv",15,1,"3","Bit","0x10","-","Meldung: aktiv"]
["IE[1]","ExBlo",15,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["IE[1]","Ex rückw Verr",15,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["IE[1]","Blo AuslBef",15,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["IE[1]","ExBlo AuslBef",15,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["IE[1]","IEH2 Blo",15,1,"3","Bit","0x200","-","Meldung: Blockade durch Inrush"]
["IE[1]","Alarm",15,1,"3","Bit","0x400","-","Meldung: Der Alarm-Schwellwert wurde überschritten."]
["IE[1]","Ausl (*)",15,1,"3","Bit","0x800","-","Meldung: Auslösung"]
["IE[1]","AuslBef (*)",15,1,"3","Bit","0x1000","-","Meldung: Auslösebefehl"]
["IE[2]","ExBlo1-E",16,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["IE[2]","ExBlo2-E",16,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["IE[2]","ExBlo AuslBef-E",16,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["IE[2]","Ex rückw Verr-E",16,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["IE[2]","Aktiv",16,1,"3","Bit","0x10","-","Meldung: aktiv"]
["IE[2]","ExBlo",16,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["IE[2]","Ex rückw Verr",16,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["IE[2]","Blo AuslBef",16,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["IE[2]","ExBlo AuslBef",16,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["IE[2]","IEH2 Blo",16,1,"3","Bit","0x200","-","Meldung: Blockade durch Inrush"]
["IE[2]","Alarm",16,1,"3","Bit","0x400","-","Meldung: Der Alarm-Schwellwert wurde überschritten."]
["IE[2]","Ausl (*)",16,1,"3","Bit","0x800","-","Meldung: Auslösung"]
["IE[2]","AuslBef (*)",16,1,"3","Bit","0x1000","-","Meldung: Auslösebefehl"]
["IE[3]","ExBlo1-E",17,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["IE[3]","ExBlo2-E",17,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["IE[3]","ExBlo AuslBef-E",17,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["IE[3]","Ex rückw Verr-E",17,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["IE[3]","Aktiv",17,1,"3","Bit","0x10","-","Meldung: aktiv"]
["IE[3]","ExBlo",17,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["IE[3]","Ex rückw Verr",17,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["IE[3]","Blo AuslBef",17,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["IE[3]","ExBlo AuslBef",17,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["IE[3]","IEH2 Blo",17,1,"3","Bit","0x200","-","Meldung: Blockade durch Inrush"]
["IE[3]","Alarm",17,1,"3","Bit","0x400","-","Meldung: Der Alarm-Schwellwert wurde überschritten."]
["IE[3]","Ausl (*)",17,1,"3","Bit","0x800","-","Meldung: Auslösung"]
["IE[3]","AuslBef (*)",17,1,"3","Bit","0x1000","-","Meldung: Auslösebefehl"]
["IE[4]","ExBlo1-E",18,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["IE[4]","ExBlo2-E",18,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["IE[4]","ExBlo AuslBef-E",18,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["IE[4]","Ex rückw Verr-E",18,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["IE[4]","Aktiv",18,1,"3","Bit","0x10","-","Meldung: aktiv"]
["IE[4]","ExBlo",18,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["IE[4]","Ex rückw Verr",18,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["IE[4]","Blo AuslBef",18,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["IE[4]","ExBlo AuslBef",18,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["IE[4]","IEH2 Blo",18,1,"3","Bit","0x200","-","Meldung: Blockade durch Inrush"]
["IE[4]","Alarm",18,1,"3","Bit","0x400","-","Meldung: Der Alarm-Schwellwert wurde überschritten."]
["IE[4]","Ausl (*)",18,1,"3","Bit","0x800","-","Meldung: Auslösung"]
["IE[4]","AuslBef (*)",18,1,"3","Bit","0x1000","-","Meldung: Auslösebefehl"]
["IH2","ExBlo1-E",22,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["IH2","ExBlo2-E",22,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["IH2","Aktiv",22,1,"3","Bit","0x4","-","Meldung: aktiv"]
["IH2","ExBlo",22,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["IH2","Blo L1",22,1,"3","Bit","0x10","-","Meldung: Blockade L1"]
["IH2","Blo L2",22,1,"3","Bit","0x20","-","Meldung: Blockade L2"]
["IH2","Blo L3",22,1,"3","Bit","0x40","-","Meldung: Blockade L3"]
["IH2","Blo IE gem",22,1,"3","Bit","0x80","-","Meldung: Blockade des Erdschutz-Moduls (gemessener Erdstrom)"]
["IH2","3-ph Blo",22,1,"3","Bit","0x100","-","Meldung: Blockierung des Auslösekommandos, da in mindestens einer Phase ein Inrush erkannt wurde."]
["IH2","Blo IE err",22,1,"3","Bit","0x200","-","Meldung: Blockade des Erdschutz-Moduls (berechneter Erdstrom)"]
["IRIG-B","IRIG-B aktiv",148,1,"3","Bit","0x1","-","Meldung: Wenn für 60 s kein gültiges IRIG-B Signal vorhanden ist, dann wird IRIG-B als inaktiv angesehen."]
["IRIG-B","High-Low Invert",148,1,"3","Bit","0x2","-","Meldung: Die High und Low Signale des IRIG-B sind invertiert. Es handelt sich hierbei NICHT um einen Verdrahtungsfehler. Bei einem Verdrahtungsfehler wird kein Signal erkannt."]
["I[1]","ExBlo1-E",3,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["I[1]","ExBlo2-E",3,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["I[1]","ExBlo AuslBef-E",3,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["I[1]","Ex rückw Verr-E",3,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["I[1]","Aktiv",3,1,"3","Bit","0x10","-","Meldung: aktiv"]
["I[1]","ExBlo",3,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["I[1]","Ex rückw Verr",3,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["I[1]","Blo AuslBef",3,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["I[1]","ExBlo AuslBef",3,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["I[1]","IH2 Blo",3,1,"3","Bit","0x200","-","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["I[1]","Alarm L1",4,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["I[1]","Alarm L2",4,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["I[1]","Alarm L3",4,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["I[1]","Alarm",4,1,"3","Bit","0x8","-","Meldung: Alarm"]
["I[1]","Ausl L1 (*)",4,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["I[1]","Ausl L2 (*)",4,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["I[1]","Ausl L3 (*)",4,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["I[1]","Ausl (*)",4,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["I[1]","AuslBef (*)",4,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["I[2]","ExBlo1-E",5,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["I[2]","ExBlo2-E",5,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["I[2]","ExBlo AuslBef-E",5,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["I[2]","Ex rückw Verr-E",5,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["I[2]","Aktiv",5,1,"3","Bit","0x10","-","Meldung: aktiv"]
["I[2]","ExBlo",5,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["I[2]","Ex rückw Verr",5,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["I[2]","Blo AuslBef",5,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["I[2]","ExBlo AuslBef",5,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["I[2]","IH2 Blo",5,1,"3","Bit","0x200","-","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["I[2]","Alarm L1",6,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["I[2]","Alarm L2",6,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["I[2]","Alarm L3",6,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["I[2]","Alarm",6,1,"3","Bit","0x8","-","Meldung: Alarm"]
["I[2]","Ausl L1 (*)",6,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["I[2]","Ausl L2 (*)",6,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["I[2]","Ausl L3 (*)",6,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["I[2]","Ausl (*)",6,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["I[2]","AuslBef (*)",6,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["I[3]","ExBlo1-E",7,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["I[3]","ExBlo2-E",7,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["I[3]","ExBlo AuslBef-E",7,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["I[3]","Ex rückw Verr-E",7,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["I[3]","Aktiv",7,1,"3","Bit","0x10","-","Meldung: aktiv"]
["I[3]","ExBlo",7,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["I[3]","Ex rückw Verr",7,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["I[3]","Blo AuslBef",7,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["I[3]","ExBlo AuslBef",7,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["I[3]","IH2 Blo",7,1,"3","Bit","0x200","-","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["I[3]","Alarm L1",8,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["I[3]","Alarm L2",8,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["I[3]","Alarm L3",8,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["I[3]","Alarm",8,1,"3","Bit","0x8","-","Meldung: Alarm"]
["I[3]","Ausl L1 (*)",8,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["I[3]","Ausl L2 (*)",8,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["I[3]","Ausl L3 (*)",8,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["I[3]","Ausl (*)",8,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["I[3]","AuslBef (*)",8,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["I[4]","ExBlo1-E",9,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["I[4]","ExBlo2-E",9,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["I[4]","ExBlo AuslBef-E",9,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["I[4]","Ex rückw Verr-E",9,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["I[4]","Aktiv",9,1,"3","Bit","0x10","-","Meldung: aktiv"]
["I[4]","ExBlo",9,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["I[4]","Ex rückw Verr",9,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["I[4]","Blo AuslBef",9,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["I[4]","ExBlo AuslBef",9,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["I[4]","IH2 Blo",9,1,"3","Bit","0x200","-","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["I[4]","Alarm L1",10,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["I[4]","Alarm L2",10,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["I[4]","Alarm L3",10,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["I[4]","Alarm",10,1,"3","Bit","0x8","-","Meldung: Alarm"]
["I[4]","Ausl L1 (*)",10,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["I[4]","Ausl L2 (*)",10,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["I[4]","Ausl L3 (*)",10,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["I[4]","Ausl (*)",10,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["I[4]","AuslBef (*)",10,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["I[5]","ExBlo1-E",11,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["I[5]","ExBlo2-E",11,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["I[5]","ExBlo AuslBef-E",11,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["I[5]","Ex rückw Verr-E",11,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["I[5]","Aktiv",11,1,"3","Bit","0x10","-","Meldung: aktiv"]
["I[5]","ExBlo",11,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["I[5]","Ex rückw Verr",11,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["I[5]","Blo AuslBef",11,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["I[5]","ExBlo AuslBef",11,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["I[5]","IH2 Blo",11,1,"3","Bit","0x200","-","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["I[5]","Alarm L1",12,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["I[5]","Alarm L2",12,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["I[5]","Alarm L3",12,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["I[5]","Alarm",12,1,"3","Bit","0x8","-","Meldung: Alarm"]
["I[5]","Ausl L1 (*)",12,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["I[5]","Ausl L2 (*)",12,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["I[5]","Ausl L3 (*)",12,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["I[5]","Ausl (*)",12,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["I[5]","AuslBef (*)",12,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["I[6]","ExBlo1-E",13,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["I[6]","ExBlo2-E",13,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["I[6]","ExBlo AuslBef-E",13,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["I[6]","Ex rückw Verr-E",13,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["I[6]","Aktiv",13,1,"3","Bit","0x10","-","Meldung: aktiv"]
["I[6]","ExBlo",13,1,"3","Bit","0x20","-","Meldung: Externe Blockade"]
["I[6]","Ex rückw Verr",13,1,"3","Bit","0x40","-","Meldung: Externe rückwärtige Verriegelung"]
["I[6]","Blo AuslBef",13,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["I[6]","ExBlo AuslBef",13,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["I[6]","IH2 Blo",13,1,"3","Bit","0x200","-","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["I[6]","Alarm L1",14,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["I[6]","Alarm L2",14,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["I[6]","Alarm L3",14,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["I[6]","Alarm",14,1,"3","Bit","0x8","-","Meldung: Alarm"]
["I[6]","Ausl L1 (*)",14,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["I[6]","Ausl L2 (*)",14,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["I[6]","Ausl L3 (*)",14,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["I[6]","Ausl (*)",14,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["I[6]","AuslBef (*)",14,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["K Slot X2","K 1",1003,1,"3","Bit","0x1","-","Meldung: Ausgangsrelais"]
["K Slot X2","K 2",1003,1,"3","Bit","0x2","-","Meldung: Ausgangsrelais"]
["K Slot X2","K 3",1003,1,"3","Bit","0x4","-","Meldung: Ausgangsrelais"]
["K Slot X2","K 4",1003,1,"3","Bit","0x8","-","Meldung: Ausgangsrelais"]
["K Slot X2","K 5",1003,1,"3","Bit","0x10","-","Meldung: Ausgangsrelais"]
["K Slot X2","K 6",1003,1,"3","Bit","0x20","-","Meldung: Ausgangsrelais"]
["K Slot X2","GESPERRT",1003,1,"3","Bit","0x40","-","Meldung: Relais GESPERRT um Wartungsarbeiten, ohne das Risiko ganze Prozesse offline zu schalten, sicher durchführen zu können (Hinweis, der Selbstüberwachungskontakt ist nicht sperrbar, kann nicht funktionslos geschaltet werden)."]
["K Slot X2","K erzwungen",1003,1,"3","Bit","0x80","-","Meldung: Der Status von mindestens einem Ausgangsrelais wurde erzwungen (entspricht  nicht dem Zustand der rangierten Signale)"]
["K Slot X4","K 1",1015,1,"3","Bit","0x1","-","Meldung: Ausgangsrelais"]
["K Slot X4","K 2",1015,1,"3","Bit","0x2","-","Meldung: Ausgangsrelais"]
["K Slot X4","K 3",1015,1,"3","Bit","0x4","-","Meldung: Ausgangsrelais"]
["K Slot X4","K 4",1015,1,"3","Bit","0x8","-","Meldung: Ausgangsrelais"]
["K Slot X4","K 5",1015,1,"3","Bit","0x10","-","Meldung: Ausgangsrelais"]
["K Slot X4","GESPERRT",1015,1,"3","Bit","0x40","-","Meldung: Relais GESPERRT um Wartungsarbeiten, ohne das Risiko ganze Prozesse offline zu schalten, sicher durchführen zu können (Hinweis, der Selbstüberwachungskontakt ist nicht sperrbar, kann nicht funktionslos geschaltet werden)."]
["K Slot X4","K erzwungen",1015,1,"3","Bit","0x80","-","Meldung: Der Status von mindestens einem Ausgangsrelais wurde erzwungen (entspricht  nicht dem Zustand der rangierten Signale)"]
["K Slot X5","K 1",1004,1,"3","Bit","0x1","-","Meldung: Ausgangsrelais"]
["K Slot X5","K 2",1004,1,"3","Bit","0x2","-","Meldung: Ausgangsrelais"]
["K Slot X5","K 3",1004,1,"3","Bit","0x4","-","Meldung: Ausgangsrelais"]
["K Slot X5","K 4",1004,1,"3","Bit","0x8","-","Meldung: Ausgangsrelais"]
["K Slot X5","K 5",1004,1,"3","Bit","0x10","-","Meldung: Ausgangsrelais"]
["K Slot X5","K 6",1004,1,"3","Bit","0x20","-","Meldung: Ausgangsrelais"]
["K Slot X5","GESPERRT",1004,1,"3","Bit","0x40","-","Meldung: Relais GESPERRT um Wartungsarbeiten, ohne das Risiko ganze Prozesse offline zu schalten, sicher durchführen zu können (Hinweis, der Selbstüberwachungskontakt ist nicht sperrbar, kann nicht funktionslos geschaltet werden)."]
["K Slot X5","K erzwungen",1004,1,"3","Bit","0x80","-","Meldung: Der Status von mindestens einem Ausgangsrelais wurde erzwungen (entspricht  nicht dem Zustand der rangierten Signale)"]
["K Slot X5","K 1",1013,1,"3","Bit","0x1","-","Meldung: Ausgangsrelais"]
["K Slot X5","K 2",1013,1,"3","Bit","0x2","-","Meldung: Ausgangsrelais"]
["K Slot X5","K 3",1013,1,"3","Bit","0x4","-","Meldung: Ausgangsrelais"]
["K Slot X5","K 4",1013,1,"3","Bit","0x8","-","Meldung: Ausgangsrelais"]
["K Slot X5","GESPERRT",1013,1,"3","Bit","0x40","-","Meldung: Relais GESPERRT um Wartungsarbeiten, ohne das Risiko ganze Prozesse offline zu schalten, sicher durchführen zu können (Hinweis, der Selbstüberwachungskontakt ist nicht sperrbar, kann nicht funktionslos geschaltet werden)."]
["K Slot X5","K erzwungen",1013,1,"3","Bit","0x80","-","Meldung: Der Status von mindestens einem Ausgangsrelais wurde erzwungen (entspricht  nicht dem Zustand der rangierten Signale)"]
["K Slot X6","K 1",1016,1,"3","Bit","0x1","-","Meldung: Ausgangsrelais"]
["K Slot X6","K 2",1016,1,"3","Bit","0x2","-","Meldung: Ausgangsrelais"]
["K Slot X6","K 3",1016,1,"3","Bit","0x4","-","Meldung: Ausgangsrelais"]
["K Slot X6","K 4",1016,1,"3","Bit","0x8","-","Meldung: Ausgangsrelais"]
["K Slot X6","GESPERRT",1016,1,"3","Bit","0x40","-","Meldung: Relais GESPERRT um Wartungsarbeiten, ohne das Risiko ganze Prozesse offline zu schalten, sicher durchführen zu können (Hinweis, der Selbstüberwachungskontakt ist nicht sperrbar, kann nicht funktionslos geschaltet werden)."]
["K Slot X6","K erzwungen",1016,1,"3","Bit","0x80","-","Meldung: Der Status von mindestens einem Ausgangsrelais wurde erzwungen (entspricht  nicht dem Zustand der rangierten Signale)"]
["KLA","ExBlo1-E",66,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["KLA","ExBlo2-E",66,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["KLA","Ex rückw Verr-E",66,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe rückwärtige Verriegelung"]
["KLA","Aktiv",66,1,"3","Bit","0x8","-","Meldung: aktiv"]
["KLA","ExBlo",66,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["KLA","Ex rückw Verr",66,1,"3","Bit","0x20","-","Meldung: Externe rückwärtige Verriegelung"]
["KLA","freigegeben",66,1,"3","Bit","0x200","-","Meldung: Kalte Last Freigabe"]
["KLA","erkannt (*)",66,1,"3","Bit","0x400","-","Meldung: Kalte Last Erkennung erkannt"]
["KLA","I<",66,1,"3","Bit","0x800","-","Meldung: Kein Laststrom."]
["KLA","AWE Blo",66,1,"3","Bit","0x1000","-","Meldung: Blockade durch AWE "]
["KLA","Last Inrush",66,1,"3","Bit","0x2000","-","Meldung: Last Inrush"]
["KLA","Beruhigungszeit",66,1,"3","Bit","0x4000","-","Meldung: Beruhigungszeit"]
["LF[1]","ExBlo1-E",73,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["LF[1]","ExBlo2-E",73,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["LF[1]","ExBlo AuslBef-E",73,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["LF[1]","Aktiv",73,1,"3","Bit","0x8","-","Meldung: aktiv"]
["LF[1]","ExBlo",73,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["LF[1]","Blo AuslBef",73,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["LF[1]","ExBlo AuslBef",73,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["LF[1]","Alarm",73,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsfaktor"]
["LF[1]","Ausl (*)",73,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsfaktor"]
["LF[1]","AuslBef (*)",73,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["LF[1]","Kompensation",73,1,"3","Bit","0x400","-","Meldung: Kompensationssignal"]
["LF[1]","nicht möglich",73,1,"3","Bit","0x800","-","Meldung: Alarm Leistungsfaktor nicht möglich"]
["LF[2]","ExBlo1-E",74,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["LF[2]","ExBlo2-E",74,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["LF[2]","ExBlo AuslBef-E",74,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["LF[2]","Aktiv",74,1,"3","Bit","0x8","-","Meldung: aktiv"]
["LF[2]","ExBlo",74,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["LF[2]","Blo AuslBef",74,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["LF[2]","ExBlo AuslBef",74,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["LF[2]","Alarm",74,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsfaktor"]
["LF[2]","Ausl (*)",74,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsfaktor"]
["LF[2]","AuslBef (*)",74,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["LF[2]","Kompensation",74,1,"3","Bit","0x400","-","Meldung: Kompensationssignal"]
["LF[2]","nicht möglich",74,1,"3","Bit","0x800","-","Meldung: Alarm Leistungsfaktor nicht möglich"]
["LS-Mitnahme","ExBlo1-E",253,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["LS-Mitnahme","ExBlo2-E",253,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["LS-Mitnahme","ExBlo AuslBef-E",253,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["LS-Mitnahme","Alarm-E",253,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Alarm"]
["LS-Mitnahme","Ausl-E",253,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Auslösebefehl"]
["LS-Mitnahme","Aktiv",253,1,"3","Bit","0x20","-","Meldung: aktiv"]
["LS-Mitnahme","ExBlo",253,1,"3","Bit","0x40","-","Meldung: Externe Blockade"]
["LS-Mitnahme","Blo AuslBef",253,1,"3","Bit","0x80","-","Meldung: Auslösebefehl blockiert"]
["LS-Mitnahme","ExBlo AuslBef",253,1,"3","Bit","0x100","-","Meldung: Externe Blockade des Auslösekommandos"]
["LS-Mitnahme","Alarm",253,1,"3","Bit","0x200","-","Meldung: Alarm"]
["LS-Mitnahme","Ausl (*)",253,1,"3","Bit","0x400","-","Meldung: Auslösung"]
["LS-Mitnahme","AuslBef (*)",253,1,"3","Bit","0x800","-","Meldung: Auslösebefehl"]
["LSV","ExBlo1-E",53,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["LSV","ExBlo2-E",53,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["LSV","Aktiv",53,1,"3","Bit","0x4","-","Meldung: aktiv"]
["LSV","ExBlo",53,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["LSV","Trigger1-E",53,1,"3","Bit","0x10","-","Moduleingang: Trigger der den LSV startet"]
["LSV","Trigger2-E",53,1,"3","Bit","0x20","-","Moduleingang: Trigger der den LSV startet"]
["LSV","Trigger3-E",53,1,"3","Bit","0x40","-","Moduleingang: Trigger der den LSV startet"]
["LSV","läuft",53,1,"3","Bit","0x80","-","Meldung: LSV-Modul gestartet"]
["LSV","Alarm (*)",53,1,"3","Bit","0x100","-","Meldung: Leistungsschalterversager"]
["LSV","Verrieg (*)",53,1,"3","Bit","0x200","-","Meldung: Verriegelung"]
["LSV","Warte auf Trigger (*)",53,1,"3","Bit","0x400","-","Warte auf Trigger"]
["LVRT[1]","ExBlo1-E",254,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["LVRT[1]","ExBlo2-E",254,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["LVRT[1]","ExBlo AuslBef-E",254,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["LVRT[1]","Aktiv",254,1,"3","Bit","0x8","-","Meldung: aktiv"]
["LVRT[1]","ExBlo",254,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["LVRT[1]","Blo AuslBef",254,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["LVRT[1]","ExBlo AuslBef",254,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["LVRT[1]","Alarm L1",255,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["LVRT[1]","Alarm L2",255,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["LVRT[1]","Alarm L3",255,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["LVRT[1]","Alarm",255,1,"3","Bit","0x8","-","Meldung: Alarm Spannungsstufe"]
["LVRT[1]","Ausl L1 (*)",255,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["LVRT[1]","Ausl L2 (*)",255,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["LVRT[1]","Ausl L3 (*)",255,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["LVRT[1]","Ausl (*)",255,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["LVRT[1]","AuslBef (*)",255,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["LVRT[1]","t-LVRT läuft (*)",255,1,"3","Bit","0x200","-","Meldung: t-LVRT läuft"]
["LVRT[2]","ExBlo1-E",270,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["LVRT[2]","ExBlo2-E",270,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["LVRT[2]","ExBlo AuslBef-E",270,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["LVRT[2]","Aktiv",270,1,"3","Bit","0x8","-","Meldung: aktiv"]
["LVRT[2]","ExBlo",270,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["LVRT[2]","Blo AuslBef",270,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["LVRT[2]","ExBlo AuslBef",270,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["LVRT[2]","Alarm L1",271,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["LVRT[2]","Alarm L2",271,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["LVRT[2]","Alarm L3",271,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["LVRT[2]","Alarm",271,1,"3","Bit","0x8","-","Meldung: Alarm Spannungsstufe"]
["LVRT[2]","Ausl L1 (*)",271,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["LVRT[2]","Ausl L2 (*)",271,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["LVRT[2]","Ausl L3 (*)",271,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["LVRT[2]","Ausl (*)",271,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["LVRT[2]","AuslBef (*)",271,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["LVRT[2]","t-LVRT läuft (*)",271,1,"3","Bit","0x200","-","Meldung: t-LVRT läuft"]
["Logik","LG1.Gatterausgang",1100,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG1.Timerausgang",1100,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG1.Ausgang",1100,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG1.Invertierter Ausg",1100,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG1.GatterEing1-E",1100,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG1.GatterEing2-E",1100,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG1.GatterEing3-E",1100,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG1.GatterEing4-E",1100,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG1.Res Selbsthaltung-E",1100,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG2.Gatterausgang",1101,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG2.Timerausgang",1101,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG2.Ausgang",1101,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG2.Invertierter Ausg",1101,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG2.GatterEing1-E",1101,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG2.GatterEing2-E",1101,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG2.GatterEing3-E",1101,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG2.GatterEing4-E",1101,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG2.Res Selbsthaltung-E",1101,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG3.Gatterausgang",1102,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG3.Timerausgang",1102,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG3.Ausgang",1102,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG3.Invertierter Ausg",1102,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG3.GatterEing1-E",1102,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG3.GatterEing2-E",1102,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG3.GatterEing3-E",1102,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG3.GatterEing4-E",1102,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG3.Res Selbsthaltung-E",1102,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG4.Gatterausgang",1103,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG4.Timerausgang",1103,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG4.Ausgang",1103,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG4.Invertierter Ausg",1103,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG4.GatterEing1-E",1103,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG4.GatterEing2-E",1103,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG4.GatterEing3-E",1103,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG4.GatterEing4-E",1103,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG4.Res Selbsthaltung-E",1103,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG5.Gatterausgang",1104,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG5.Timerausgang",1104,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG5.Ausgang",1104,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG5.Invertierter Ausg",1104,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG5.GatterEing1-E",1104,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG5.GatterEing2-E",1104,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG5.GatterEing3-E",1104,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG5.GatterEing4-E",1104,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG5.Res Selbsthaltung-E",1104,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG6.Gatterausgang",1105,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG6.Timerausgang",1105,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG6.Ausgang",1105,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG6.Invertierter Ausg",1105,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG6.GatterEing1-E",1105,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG6.GatterEing2-E",1105,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG6.GatterEing3-E",1105,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG6.GatterEing4-E",1105,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG6.Res Selbsthaltung-E",1105,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG7.Gatterausgang",1106,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG7.Timerausgang",1106,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG7.Ausgang",1106,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG7.Invertierter Ausg",1106,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG7.GatterEing1-E",1106,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG7.GatterEing2-E",1106,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG7.GatterEing3-E",1106,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG7.GatterEing4-E",1106,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG7.Res Selbsthaltung-E",1106,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG8.Gatterausgang",1107,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG8.Timerausgang",1107,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG8.Ausgang",1107,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG8.Invertierter Ausg",1107,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG8.GatterEing1-E",1107,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG8.GatterEing2-E",1107,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG8.GatterEing3-E",1107,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG8.GatterEing4-E",1107,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG8.Res Selbsthaltung-E",1107,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG9.Gatterausgang",1108,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG9.Timerausgang",1108,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG9.Ausgang",1108,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG9.Invertierter Ausg",1108,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG9.GatterEing1-E",1108,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG9.GatterEing2-E",1108,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG9.GatterEing3-E",1108,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG9.GatterEing4-E",1108,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG9.Res Selbsthaltung-E",1108,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG10.Gatterausgang",1109,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG10.Timerausgang",1109,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG10.Ausgang",1109,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG10.Invertierter Ausg",1109,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG10.GatterEing1-E",1109,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG10.GatterEing2-E",1109,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG10.GatterEing3-E",1109,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG10.GatterEing4-E",1109,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG10.Res Selbsthaltung-E",1109,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG11.Gatterausgang",1110,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG11.Timerausgang",1110,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG11.Ausgang",1110,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG11.Invertierter Ausg",1110,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG11.GatterEing1-E",1110,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG11.GatterEing2-E",1110,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG11.GatterEing3-E",1110,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG11.GatterEing4-E",1110,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG11.Res Selbsthaltung-E",1110,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG12.Gatterausgang",1111,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG12.Timerausgang",1111,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG12.Ausgang",1111,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG12.Invertierter Ausg",1111,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG12.GatterEing1-E",1111,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG12.GatterEing2-E",1111,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG12.GatterEing3-E",1111,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG12.GatterEing4-E",1111,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG12.Res Selbsthaltung-E",1111,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG13.Gatterausgang",1112,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG13.Timerausgang",1112,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG13.Ausgang",1112,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG13.Invertierter Ausg",1112,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG13.GatterEing1-E",1112,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG13.GatterEing2-E",1112,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG13.GatterEing3-E",1112,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG13.GatterEing4-E",1112,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG13.Res Selbsthaltung-E",1112,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG14.Gatterausgang",1113,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG14.Timerausgang",1113,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG14.Ausgang",1113,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG14.Invertierter Ausg",1113,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG14.GatterEing1-E",1113,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG14.GatterEing2-E",1113,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG14.GatterEing3-E",1113,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG14.GatterEing4-E",1113,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG14.Res Selbsthaltung-E",1113,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG15.Gatterausgang",1114,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG15.Timerausgang",1114,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG15.Ausgang",1114,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG15.Invertierter Ausg",1114,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG15.GatterEing1-E",1114,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG15.GatterEing2-E",1114,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG15.GatterEing3-E",1114,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG15.GatterEing4-E",1114,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG15.Res Selbsthaltung-E",1114,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG16.Gatterausgang",1115,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG16.Timerausgang",1115,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG16.Ausgang",1115,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG16.Invertierter Ausg",1115,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG16.GatterEing1-E",1115,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG16.GatterEing2-E",1115,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG16.GatterEing3-E",1115,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG16.GatterEing4-E",1115,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG16.Res Selbsthaltung-E",1115,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG17.Gatterausgang",1116,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG17.Timerausgang",1116,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG17.Ausgang",1116,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG17.Invertierter Ausg",1116,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG17.GatterEing1-E",1116,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG17.GatterEing2-E",1116,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG17.GatterEing3-E",1116,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG17.GatterEing4-E",1116,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG17.Res Selbsthaltung-E",1116,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG18.Gatterausgang",1117,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG18.Timerausgang",1117,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG18.Ausgang",1117,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG18.Invertierter Ausg",1117,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG18.GatterEing1-E",1117,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG18.GatterEing2-E",1117,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG18.GatterEing3-E",1117,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG18.GatterEing4-E",1117,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG18.Res Selbsthaltung-E",1117,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG19.Gatterausgang",1118,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG19.Timerausgang",1118,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG19.Ausgang",1118,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG19.Invertierter Ausg",1118,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG19.GatterEing1-E",1118,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG19.GatterEing2-E",1118,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG19.GatterEing3-E",1118,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG19.GatterEing4-E",1118,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG19.Res Selbsthaltung-E",1118,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Logik","LG20.Gatterausgang",1119,1,"3","Bit","0x1","-","Meldung: Ausgang des Logikgatters"]
["Logik","LG20.Timerausgang",1119,1,"3","Bit","0x2","-","Meldung: Ausgang des Timers"]
["Logik","LG20.Ausgang",1119,1,"3","Bit","0x4","-","Meldung: Selbsthaltung des Ausgangs (Q)"]
["Logik","LG20.Invertierter Ausg",1119,1,"3","Bit","0x8","-","Meldung: Negierte Selbsthaltung des Ausgangs (Q NOT)"]
["Logik","LG20.GatterEing1-E",1119,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG20.GatterEing2-E",1119,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG20.GatterEing3-E",1119,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG20.GatterEing4-E",1119,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Rangierung des Eingangssignals"]
["Logik","LG20.Res Selbsthaltung-E",1119,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Rücksetzsignal für die Selbsthaltung."]
["Modbus","Leittechnik-Bef 1",1005,1,"3","Bit","0x1","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 2",1005,1,"3","Bit","0x2","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 3",1005,1,"3","Bit","0x4","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 4",1005,1,"3","Bit","0x8","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 5",1005,1,"3","Bit","0x10","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 6",1005,1,"3","Bit","0x20","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 7",1005,1,"3","Bit","0x40","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 8",1005,1,"3","Bit","0x80","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 9",1005,1,"3","Bit","0x100","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 10",1005,1,"3","Bit","0x200","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 11",1005,1,"3","Bit","0x400","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 12",1005,1,"3","Bit","0x800","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 13",1005,1,"3","Bit","0x1000","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 14",1005,1,"3","Bit","0x2000","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 15",1005,1,"3","Bit","0x4000","-","Leittechnik-Befehl"]
["Modbus","Leittechnik-Bef 16",1005,1,"3","Bit","0x8000","-","Leittechnik-Befehl"]
["P","ExBlo1-E",251,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["P","ExBlo2-E",251,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["P","ExBlo AuslBef-E",251,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["P","Aktiv",251,1,"3","Bit","0x8","-","Meldung: aktiv"]
["P","ExBlo",251,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["P","Blo AuslBef",251,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["P","ExBlo AuslBef",251,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["P","Alarm",251,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsschutz"]
["P","Ausl (*)",251,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsschutz"]
["P","AuslBef (*)",251,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["PQSZ","Z Ülf Wp+",60,1,"3","Bit","0x1","-","Meldung: Zählerüberlauf Wp+"]
["PQSZ","Z Ülf Wp-",60,1,"3","Bit","0x2","-","Meldung: Zählerüberlauf Wp-"]
["PQSZ","Z Ülf Wq+",60,1,"3","Bit","0x4","-","Meldung: Zählerüberlauf Wq+"]
["PQSZ","Z Ülf Wq-",60,1,"3","Bit","0x8","-","Meldung: Zählerüberlauf Wq-"]
["PQSZ","Z Ülf Wp Net",60,1,"3","Bit","0x10","-","Meldung: Zählerüberlauf Wp Net"]
["PQSZ","Z Ülf Wq Net",60,1,"3","Bit","0x20","-","Meldung: Zählerüberlauf Wq Net"]
["PQSZ","Z Ülf Ws Net",60,1,"3","Bit","0x40","-","Meldung: Zählerüberlauf Ws Net"]
["PQSZ","Z ÜlfW Wp+",60,1,"3","Bit","0x80","-","Meldung: Zähler Wp+ wird in Kürze überlaufen"]
["PQSZ","Z ÜlfW Wp-",60,1,"3","Bit","0x100","-","Meldung: Zähler Wp- wird in Kürze überlaufen"]
["PQSZ","Z ÜlfW Wq+",60,1,"3","Bit","0x200","-","Meldung: Zähler Wq+ wird in Kürze überlaufen"]
["PQSZ","Z ÜlfW Wq-",60,1,"3","Bit","0x400","-","Meldung: Zähler Wq- wird in Kürze überlaufen"]
["PQSZ","Z ÜlfW Wp Net",60,1,"3","Bit","0x800","-","Meldung: Zähler Wp Net wird in Kürze überlaufen"]
["PQSZ","Z ÜlfW Wq Net",60,1,"3","Bit","0x1000","-","Meldung: Zähler Wq Net wird in Kürze überlaufen"]
["PQSZ","Z Ülf Ws Net",60,1,"3","Bit","0x2000","-","Meldung: Zähler Ws Net wird in Kürze überlaufen"]
["PQS[1]","ExBlo1-E",67,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[1]","ExBlo2-E",67,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[1]","ExBlo AuslBef-E",67,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["PQS[1]","Aktiv",67,1,"3","Bit","0x8","-","Meldung: aktiv"]
["PQS[1]","ExBlo",67,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["PQS[1]","Blo AuslBef",67,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["PQS[1]","ExBlo AuslBef",67,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["PQS[1]","Alarm",67,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsschutz"]
["PQS[1]","Ausl (*)",67,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsschutz"]
["PQS[1]","AuslBef (*)",67,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["PQS[2]","ExBlo1-E",68,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[2]","ExBlo2-E",68,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[2]","ExBlo AuslBef-E",68,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["PQS[2]","Aktiv",68,1,"3","Bit","0x8","-","Meldung: aktiv"]
["PQS[2]","ExBlo",68,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["PQS[2]","Blo AuslBef",68,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["PQS[2]","ExBlo AuslBef",68,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["PQS[2]","Alarm",68,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsschutz"]
["PQS[2]","Ausl (*)",68,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsschutz"]
["PQS[2]","AuslBef (*)",68,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["PQS[3]","ExBlo1-E",69,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[3]","ExBlo2-E",69,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[3]","ExBlo AuslBef-E",69,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["PQS[3]","Aktiv",69,1,"3","Bit","0x8","-","Meldung: aktiv"]
["PQS[3]","ExBlo",69,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["PQS[3]","Blo AuslBef",69,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["PQS[3]","ExBlo AuslBef",69,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["PQS[3]","Alarm",69,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsschutz"]
["PQS[3]","Ausl (*)",69,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsschutz"]
["PQS[3]","AuslBef (*)",69,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["PQS[4]","ExBlo1-E",70,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[4]","ExBlo2-E",70,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[4]","ExBlo AuslBef-E",70,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["PQS[4]","Aktiv",70,1,"3","Bit","0x8","-","Meldung: aktiv"]
["PQS[4]","ExBlo",70,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["PQS[4]","Blo AuslBef",70,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["PQS[4]","ExBlo AuslBef",70,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["PQS[4]","Alarm",70,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsschutz"]
["PQS[4]","Ausl (*)",70,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsschutz"]
["PQS[4]","AuslBef (*)",70,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["PQS[5]","ExBlo1-E",71,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[5]","ExBlo2-E",71,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[5]","ExBlo AuslBef-E",71,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["PQS[5]","Aktiv",71,1,"3","Bit","0x8","-","Meldung: aktiv"]
["PQS[5]","ExBlo",71,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["PQS[5]","Blo AuslBef",71,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["PQS[5]","ExBlo AuslBef",71,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["PQS[5]","Alarm",71,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsschutz"]
["PQS[5]","Ausl (*)",71,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsschutz"]
["PQS[5]","AuslBef (*)",71,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["PQS[6]","ExBlo1-E",72,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[6]","ExBlo2-E",72,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["PQS[6]","ExBlo AuslBef-E",72,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["PQS[6]","Aktiv",72,1,"3","Bit","0x8","-","Meldung: aktiv"]
["PQS[6]","ExBlo",72,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["PQS[6]","Blo AuslBef",72,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["PQS[6]","ExBlo AuslBef",72,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["PQS[6]","Alarm",72,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsschutz"]
["PQS[6]","Ausl (*)",72,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsschutz"]
["PQS[6]","AuslBef (*)",72,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["Q","ExBlo1-E",252,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["Q","ExBlo2-E",252,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade"]
["Q","ExBlo AuslBef-E",252,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["Q","Aktiv",252,1,"3","Bit","0x8","-","Meldung: aktiv"]
["Q","ExBlo",252,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["Q","Blo AuslBef",252,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["Q","ExBlo AuslBef",252,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["Q","Alarm",252,1,"3","Bit","0x80","-","Meldung: Alarm Leistungsschutz"]
["Q","Ausl (*)",252,1,"3","Bit","0x100","-","Meldung: Auslösung Leistungsschutz"]
["Q","AuslBef (*)",252,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["Q->&U<","ExBlo1-E",157,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["Q->&U<","ExBlo2-E",157,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["Q->&U<","Aktiv",157,1,"3","Bit","0x4","-","Meldung: aktiv"]
["Q->&U<","ExBlo",157,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["Q->&U<","Autom Spw Blo",157,1,"3","Bit","0x10","-","Meldung: Blockade durch Spannungswandlerfehler (Automatenfall)"]
["Q->&U<","Alarm",157,1,"3","Bit","0x20","-","Meldung: Alarm Blindleistungsunterspannungsschutz"]
["Q->&U<","Entkuppl. NAP",157,1,"3","Bit","0x200","-","Meldung:  Entkupplung am Netzanschlusspunkts"]
["Q->&U<","Entkuppl. EZE",157,1,"3","Bit","0x400","-","Meldung: Entkupplung der Erzeugungseinheit"]
["SG[1]","Hiko AUS-E",177,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52b)"]
["SG[1]","Hiko EIN-E",177,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52a)"]
["SG[1]","Bereit-E",177,1,"3","Bit","0x4","-","Zustand des Moduleingangs: LS bereit"]
["SG[1]","Sys-in-Sync-E",177,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Innerhalb der Synchronisierzeit muss dieses Signal anstehen, damit zugeschaltet wird. Anderfalls war der Schaltversuch erfolglos."]
["SG[1]","Verrieg AUS1-E",177,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[1]","Verrieg AUS2-E",177,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[1]","Verrieg AUS3-E",177,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[1]","Verrieg EIN1-E",177,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[1]","Verrieg EIN2-E",177,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[1]","Verrieg EIN3-E",177,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[1]","SBef AUS-E",177,1,"3","Bit","0x800","-","Zustand des Moduleingangs: Ausschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[1]","SBef EIN-E",177,1,"3","Bit","0x1000","-","Zustand des Moduleingangs: Einschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[1]","AuslBef (*)",177,1,"3","Bit","0x2000","-","Meldung: Auslösebefehl"]
["SG[1]","AUS Bef",177,1,"3","Bit","0x4000","-","Meldung: Ausschaltbefehl an das Schaltgerät. Dieser Ausschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze AUS-Kommando beinhalten."]
["SG[1]","AUS Bef manuell",177,1,"3","Bit","0x8000","-","Meldung: Manueller Ausschaltbefehl"]
["SG[1]","EIN Bef",178,1,"3","Bit","0x1","-","Meldung: Einschaltbefehl an das Schaltgerät. Dieser Einschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze EIN-Kommando beinhalten."]
["SG[1]","EIN Bef  manuell",178,1,"3","Bit","0x2","-","Meldung: Manueller Einschaltbefehl"]
["SG[1]","Sync EIN Anforderung",178,1,"3","Bit","0x4","-","Meldung: Anforderung synchronen Zuschaltens"]
["SG[1]","SGMon SGverzögert",178,1,"3","Bit","0x8","-","Meldung: Schaltgerätewartung: Alarm, der Schalter wird langsamer"]
["SG[1]","Res SGMon Sgverz",178,1,"3","Bit","0x10","-","Meldung: Rücksetzen der Meldung des verlangsamten Schalters"]
["SG[1]","SBÜ Störstellung",178,1,"3","Bit","0x40","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos. Schaltgerät in Störstellung."]
["SG[1]","SBÜ Feldverrieg",178,1,"3","Bit","0x80","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl verstößt gegen eine Feldverriegelung."]
["SG[1]","SBÜ EIN währd AUSBef",178,1,"3","Bit","0x400","-","Meldung: Schaltbefehlsüberwachung: Während ein Ausschaltbefehl aussteht, kommt ein Einschaltbefehl."]
["SG[1]","SBÜ Schaltrichtg",178,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung bzw Schaltrichtungsüberwachung: Dieses Signal wird wahr, wenn die Position, in der sich ein Schaltgerät befindet erneut angesteuert werden soll. Beispiel: Ein Schaltgerät, das sich bereits in der \"AUS\"-Position befindet, soll erneut \"AUS\"-geschaltet werden. Das Gleiche gilt für EIN-Kommandos."]
["SG[1]","SBÜ SG n. bereit",178,1,"3","Bit","0x1000","-","Meldung: Schaltbefehlsüberwachung: Das Schaltgerät ist nicht bereit."]
["SG[1]","SBÜ SyncTimeout",178,1,"3","Bit","0x2000","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl wurde nicht ausgeführt. Es wurde während der Synchronisierzeit kein Synchronisiersignal empfangen."]
["SG[1]","SBÜ erfolgreich",178,1,"3","Bit","0x4000","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolgreich"]
["SG[1]","Schutz EIN",178,1,"3","Bit","0x8000","-","Meldung: EIN Kommando durch das Schutzmodul"]
["SG[1]","Pos Gestört",179,1,"3","Bit","0x1","-","Meldung: Leistungsschalter Fehler - Unklare Schalterstellung. Die Stellungskontakte widersprechen  sich.  Nach Ablauf des Timers wird dieser Alarm ausgegeben."]
["SG[1]","t-Nachdrück",179,1,"3","Bit","0x2","-","Meldung: Nachdrückzeit"]
["SG[1]","Pos Unbest",179,1,"3","Bit","0x4","-","Meldung: Leistungsschalterstellung ist unbestimmt."]
["SG[1]","Pos AUS",179,1,"3","Bit","0x8","-","Meldung: Leistungsschalter ist in AUS-Position"]
["SG[1]","Pos EIN",179,1,"3","Bit","0x10","-","Meldung: Leistungsschalter ist in EIN-Position"]
["SG[1]","Bereit",179,1,"3","Bit","0x20","-","Meldung: Leistungsschalter ist schaltbereit."]
["SG[1]","Pos nicht EIN",179,1,"3","Bit","0x40","-","Meldung: Pos nicht EIN"]
["SG[1]","EKA Nur ein HIKO",179,1,"3","Bit","0x80","-","Meldung: Die Position des Schaltgeräts wird nur über einen einzelnen Hilfskontakt (Einpolige-Kontakt-Anzeige) erfasst. Zwischen- oder Störstellungen können auf diese Weise nicht erfasst werden."]
["SG[1]","Stellgsmeldg manipul",179,1,"3","Bit","0x100","-","Meldung: Stellungsmeldung manipuliert"]
["SG[1]","AUS inkl Schutz AUS",179,1,"3","Bit","0x200","-","Meldung: Das AUS-Kommando beinhaltet die durch den Schutz abgegebenen AUS-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[1]","EIN inkl Schutz EIN",179,1,"3","Bit","0x400","-","Meldung: Das EIN-Kommando beinhaltet die durch den Schutz abgegebenen EIN-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[1]","SBÜ Fehler AUSBef",179,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung: Wegen eines anstehenden Auslösebefehl wurde der Ausschaltbefehl nicht ausgeführt."]
["SG[1]","Verrieg AUS",179,1,"3","Bit","0x1000","-","Meldung: Mindestens ein AUS-Schaltbefehl ist verriegelt."]
["SG[1]","Verrieg EIN",179,1,"3","Bit","0x2000","-","Meldung: Mindestens ein EIN-Schaltbefehl ist verriegelt."]
["SG[1]","Sum Abschalt",195,1,"3","Bit","0x10","-","Meldung: Höchstzulässige Summe der Abschaltströme wurde in mindestens einer Phase überschritten"]
["SG[1]","Sum Abschalt:  IL1",195,1,"3","Bit","0x20","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL1"]
["SG[1]","Sum Abschalt:  IL2",195,1,"3","Bit","0x40","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL2"]
["SG[1]","Sum Abschalt:  IL3",195,1,"3","Bit","0x80","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL3"]
["SG[1]","Anz Schaltsp Alarm",195,1,"3","Bit","0x100","-","Meldung: Zu viele Schaltspiele. (Der Zählerstand »AuslBef Z« hat den unter »Anz Schaltsp Alarm« eingestellten Wert überschritten.)"]
["SG[1]","SGWartAlarm",195,1,"3","Bit","0x200","-","Meldung: Schwelle für den Revisions-Alarm"]
["SG[1]","SGWartVerrieg",195,1,"3","Bit","0x400","-","Meldung: Schwelle für die Verriegelung"]
["SG[1]","Sum Ik/h Alarm",195,1,"3","Bit","0x800","-","Meldung: Alarm, die Summe (kumuliert) der pro Stunde zulässigen Abschaltströme wurde überschritten."]
["SG[1]","Entnommen-E",256,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Leistungsschalter entnommen."]
["SG[1]","SBÜ SG entnommen",256,1,"3","Bit","0x2","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos, da Schaltgerät entnommen."]
["SG[1]","Entnommen",256,1,"3","Bit","0x4","-","Meldung: Leistungsschalter entnommen."]
["SG[2]","Hiko AUS-E",180,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52b)"]
["SG[2]","Hiko EIN-E",180,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52a)"]
["SG[2]","Bereit-E",180,1,"3","Bit","0x4","-","Zustand des Moduleingangs: LS bereit"]
["SG[2]","Sys-in-Sync-E",180,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Innerhalb der Synchronisierzeit muss dieses Signal anstehen, damit zugeschaltet wird. Anderfalls war der Schaltversuch erfolglos."]
["SG[2]","Verrieg AUS1-E",180,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[2]","Verrieg AUS2-E",180,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[2]","Verrieg AUS3-E",180,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[2]","Verrieg EIN1-E",180,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[2]","Verrieg EIN2-E",180,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[2]","Verrieg EIN3-E",180,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[2]","SBef AUS-E",180,1,"3","Bit","0x800","-","Zustand des Moduleingangs: Ausschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[2]","SBef EIN-E",180,1,"3","Bit","0x1000","-","Zustand des Moduleingangs: Einschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[2]","AuslBef (*)",180,1,"3","Bit","0x2000","-","Meldung: Auslösebefehl"]
["SG[2]","AUS Bef",180,1,"3","Bit","0x4000","-","Meldung: Ausschaltbefehl an das Schaltgerät. Dieser Ausschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze AUS-Kommando beinhalten."]
["SG[2]","AUS Bef manuell",180,1,"3","Bit","0x8000","-","Meldung: Manueller Ausschaltbefehl"]
["SG[2]","EIN Bef",181,1,"3","Bit","0x1","-","Meldung: Einschaltbefehl an das Schaltgerät. Dieser Einschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze EIN-Kommando beinhalten."]
["SG[2]","EIN Bef  manuell",181,1,"3","Bit","0x2","-","Meldung: Manueller Einschaltbefehl"]
["SG[2]","Sync EIN Anforderung",181,1,"3","Bit","0x4","-","Meldung: Anforderung synchronen Zuschaltens"]
["SG[2]","SGMon SGverzögert",181,1,"3","Bit","0x8","-","Meldung: Schaltgerätewartung: Alarm, der Schalter wird langsamer"]
["SG[2]","Res SGMon Sgverz",181,1,"3","Bit","0x10","-","Meldung: Rücksetzen der Meldung des verlangsamten Schalters"]
["SG[2]","SBÜ Störstellung",181,1,"3","Bit","0x40","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos. Schaltgerät in Störstellung."]
["SG[2]","SBÜ Feldverrieg",181,1,"3","Bit","0x80","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl verstößt gegen eine Feldverriegelung."]
["SG[2]","SBÜ EIN währd AUSBef",181,1,"3","Bit","0x400","-","Meldung: Schaltbefehlsüberwachung: Während ein Ausschaltbefehl aussteht, kommt ein Einschaltbefehl."]
["SG[2]","SBÜ Schaltrichtg",181,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung bzw Schaltrichtungsüberwachung: Dieses Signal wird wahr, wenn die Position, in der sich ein Schaltgerät befindet erneut angesteuert werden soll. Beispiel: Ein Schaltgerät, das sich bereits in der \"AUS\"-Position befindet, soll erneut \"AUS\"-geschaltet werden. Das Gleiche gilt für EIN-Kommandos."]
["SG[2]","SBÜ SG n. bereit",181,1,"3","Bit","0x1000","-","Meldung: Schaltbefehlsüberwachung: Das Schaltgerät ist nicht bereit."]
["SG[2]","SBÜ SyncTimeout",181,1,"3","Bit","0x2000","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl wurde nicht ausgeführt. Es wurde während der Synchronisierzeit kein Synchronisiersignal empfangen."]
["SG[2]","SBÜ erfolgreich",181,1,"3","Bit","0x4000","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolgreich"]
["SG[2]","Schutz EIN",181,1,"3","Bit","0x8000","-","Meldung: EIN Kommando durch das Schutzmodul"]
["SG[2]","Pos Gestört",182,1,"3","Bit","0x1","-","Meldung: Leistungsschalter Fehler - Unklare Schalterstellung. Die Stellungskontakte widersprechen  sich.  Nach Ablauf des Timers wird dieser Alarm ausgegeben."]
["SG[2]","t-Nachdrück",182,1,"3","Bit","0x2","-","Meldung: Nachdrückzeit"]
["SG[2]","Pos Unbest",182,1,"3","Bit","0x4","-","Meldung: Leistungsschalterstellung ist unbestimmt."]
["SG[2]","Pos AUS",182,1,"3","Bit","0x8","-","Meldung: Leistungsschalter ist in AUS-Position"]
["SG[2]","Pos EIN",182,1,"3","Bit","0x10","-","Meldung: Leistungsschalter ist in EIN-Position"]
["SG[2]","Bereit",182,1,"3","Bit","0x20","-","Meldung: Leistungsschalter ist schaltbereit."]
["SG[2]","Pos nicht EIN",182,1,"3","Bit","0x40","-","Meldung: Pos nicht EIN"]
["SG[2]","EKA Nur ein HIKO",182,1,"3","Bit","0x80","-","Meldung: Die Position des Schaltgeräts wird nur über einen einzelnen Hilfskontakt (Einpolige-Kontakt-Anzeige) erfasst. Zwischen- oder Störstellungen können auf diese Weise nicht erfasst werden."]
["SG[2]","Stellgsmeldg manipul",182,1,"3","Bit","0x100","-","Meldung: Stellungsmeldung manipuliert"]
["SG[2]","AUS inkl Schutz AUS",182,1,"3","Bit","0x200","-","Meldung: Das AUS-Kommando beinhaltet die durch den Schutz abgegebenen AUS-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[2]","EIN inkl Schutz EIN",182,1,"3","Bit","0x400","-","Meldung: Das EIN-Kommando beinhaltet die durch den Schutz abgegebenen EIN-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[2]","SBÜ Fehler AUSBef",182,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung: Wegen eines anstehenden Auslösebefehl wurde der Ausschaltbefehl nicht ausgeführt."]
["SG[2]","Verrieg AUS",182,1,"3","Bit","0x1000","-","Meldung: Mindestens ein AUS-Schaltbefehl ist verriegelt."]
["SG[2]","Verrieg EIN",182,1,"3","Bit","0x2000","-","Meldung: Mindestens ein EIN-Schaltbefehl ist verriegelt."]
["SG[2]","Sum Abschalt",196,1,"3","Bit","0x10","-","Meldung: Höchstzulässige Summe der Abschaltströme wurde in mindestens einer Phase überschritten"]
["SG[2]","Sum Abschalt:  IL1",196,1,"3","Bit","0x20","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL1"]
["SG[2]","Sum Abschalt:  IL2",196,1,"3","Bit","0x40","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL2"]
["SG[2]","Sum Abschalt:  IL3",196,1,"3","Bit","0x80","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL3"]
["SG[2]","Anz Schaltsp Alarm",196,1,"3","Bit","0x100","-","Meldung: Zu viele Schaltspiele. (Der Zählerstand »AuslBef Z« hat den unter »Anz Schaltsp Alarm« eingestellten Wert überschritten.)"]
["SG[2]","SGWartAlarm",196,1,"3","Bit","0x200","-","Meldung: Schwelle für den Revisions-Alarm"]
["SG[2]","SGWartVerrieg",196,1,"3","Bit","0x400","-","Meldung: Schwelle für die Verriegelung"]
["SG[2]","Sum Ik/h Alarm",196,1,"3","Bit","0x800","-","Meldung: Alarm, die Summe (kumuliert) der pro Stunde zulässigen Abschaltströme wurde überschritten."]
["SG[2]","Entnommen-E",257,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Leistungsschalter entnommen."]
["SG[2]","SBÜ SG entnommen",257,1,"3","Bit","0x2","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos, da Schaltgerät entnommen."]
["SG[2]","Entnommen",257,1,"3","Bit","0x4","-","Meldung: Leistungsschalter entnommen."]
["SG[3]","Hiko AUS-E",183,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52b)"]
["SG[3]","Hiko EIN-E",183,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52a)"]
["SG[3]","Bereit-E",183,1,"3","Bit","0x4","-","Zustand des Moduleingangs: LS bereit"]
["SG[3]","Sys-in-Sync-E",183,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Innerhalb der Synchronisierzeit muss dieses Signal anstehen, damit zugeschaltet wird. Anderfalls war der Schaltversuch erfolglos."]
["SG[3]","Verrieg AUS1-E",183,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[3]","Verrieg AUS2-E",183,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[3]","Verrieg AUS3-E",183,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[3]","Verrieg EIN1-E",183,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[3]","Verrieg EIN2-E",183,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[3]","Verrieg EIN3-E",183,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[3]","SBef AUS-E",183,1,"3","Bit","0x800","-","Zustand des Moduleingangs: Ausschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[3]","SBef EIN-E",183,1,"3","Bit","0x1000","-","Zustand des Moduleingangs: Einschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[3]","AuslBef (*)",183,1,"3","Bit","0x2000","-","Meldung: Auslösebefehl"]
["SG[3]","AUS Bef",183,1,"3","Bit","0x4000","-","Meldung: Ausschaltbefehl an das Schaltgerät. Dieser Ausschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze AUS-Kommando beinhalten."]
["SG[3]","AUS Bef manuell",183,1,"3","Bit","0x8000","-","Meldung: Manueller Ausschaltbefehl"]
["SG[3]","EIN Bef",184,1,"3","Bit","0x1","-","Meldung: Einschaltbefehl an das Schaltgerät. Dieser Einschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze EIN-Kommando beinhalten."]
["SG[3]","EIN Bef  manuell",184,1,"3","Bit","0x2","-","Meldung: Manueller Einschaltbefehl"]
["SG[3]","Sync EIN Anforderung",184,1,"3","Bit","0x4","-","Meldung: Anforderung synchronen Zuschaltens"]
["SG[3]","SGMon SGverzögert",184,1,"3","Bit","0x8","-","Meldung: Schaltgerätewartung: Alarm, der Schalter wird langsamer"]
["SG[3]","Res SGMon Sgverz",184,1,"3","Bit","0x10","-","Meldung: Rücksetzen der Meldung des verlangsamten Schalters"]
["SG[3]","SBÜ Störstellung",184,1,"3","Bit","0x40","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos. Schaltgerät in Störstellung."]
["SG[3]","SBÜ Feldverrieg",184,1,"3","Bit","0x80","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl verstößt gegen eine Feldverriegelung."]
["SG[3]","SBÜ EIN währd AUSBef",184,1,"3","Bit","0x400","-","Meldung: Schaltbefehlsüberwachung: Während ein Ausschaltbefehl aussteht, kommt ein Einschaltbefehl."]
["SG[3]","SBÜ Schaltrichtg",184,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung bzw Schaltrichtungsüberwachung: Dieses Signal wird wahr, wenn die Position, in der sich ein Schaltgerät befindet erneut angesteuert werden soll. Beispiel: Ein Schaltgerät, das sich bereits in der \"AUS\"-Position befindet, soll erneut \"AUS\"-geschaltet werden. Das Gleiche gilt für EIN-Kommandos."]
["SG[3]","SBÜ SG n. bereit",184,1,"3","Bit","0x1000","-","Meldung: Schaltbefehlsüberwachung: Das Schaltgerät ist nicht bereit."]
["SG[3]","SBÜ SyncTimeout",184,1,"3","Bit","0x2000","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl wurde nicht ausgeführt. Es wurde während der Synchronisierzeit kein Synchronisiersignal empfangen."]
["SG[3]","SBÜ erfolgreich",184,1,"3","Bit","0x4000","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolgreich"]
["SG[3]","Schutz EIN",184,1,"3","Bit","0x8000","-","Meldung: EIN Kommando durch das Schutzmodul"]
["SG[3]","Pos Gestört",185,1,"3","Bit","0x1","-","Meldung: Leistungsschalter Fehler - Unklare Schalterstellung. Die Stellungskontakte widersprechen  sich.  Nach Ablauf des Timers wird dieser Alarm ausgegeben."]
["SG[3]","t-Nachdrück",185,1,"3","Bit","0x2","-","Meldung: Nachdrückzeit"]
["SG[3]","Pos Unbest",185,1,"3","Bit","0x4","-","Meldung: Leistungsschalterstellung ist unbestimmt."]
["SG[3]","Pos AUS",185,1,"3","Bit","0x8","-","Meldung: Leistungsschalter ist in AUS-Position"]
["SG[3]","Pos EIN",185,1,"3","Bit","0x10","-","Meldung: Leistungsschalter ist in EIN-Position"]
["SG[3]","Bereit",185,1,"3","Bit","0x20","-","Meldung: Leistungsschalter ist schaltbereit."]
["SG[3]","Pos nicht EIN",185,1,"3","Bit","0x40","-","Meldung: Pos nicht EIN"]
["SG[3]","EKA Nur ein HIKO",185,1,"3","Bit","0x80","-","Meldung: Die Position des Schaltgeräts wird nur über einen einzelnen Hilfskontakt (Einpolige-Kontakt-Anzeige) erfasst. Zwischen- oder Störstellungen können auf diese Weise nicht erfasst werden."]
["SG[3]","Stellgsmeldg manipul",185,1,"3","Bit","0x100","-","Meldung: Stellungsmeldung manipuliert"]
["SG[3]","AUS inkl Schutz AUS",185,1,"3","Bit","0x200","-","Meldung: Das AUS-Kommando beinhaltet die durch den Schutz abgegebenen AUS-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[3]","EIN inkl Schutz EIN",185,1,"3","Bit","0x400","-","Meldung: Das EIN-Kommando beinhaltet die durch den Schutz abgegebenen EIN-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[3]","SBÜ Fehler AUSBef",185,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung: Wegen eines anstehenden Auslösebefehl wurde der Ausschaltbefehl nicht ausgeführt."]
["SG[3]","Verrieg AUS",185,1,"3","Bit","0x1000","-","Meldung: Mindestens ein AUS-Schaltbefehl ist verriegelt."]
["SG[3]","Verrieg EIN",185,1,"3","Bit","0x2000","-","Meldung: Mindestens ein EIN-Schaltbefehl ist verriegelt."]
["SG[3]","Sum Abschalt",197,1,"3","Bit","0x10","-","Meldung: Höchstzulässige Summe der Abschaltströme wurde in mindestens einer Phase überschritten"]
["SG[3]","Sum Abschalt:  IL1",197,1,"3","Bit","0x20","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL1"]
["SG[3]","Sum Abschalt:  IL2",197,1,"3","Bit","0x40","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL2"]
["SG[3]","Sum Abschalt:  IL3",197,1,"3","Bit","0x80","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL3"]
["SG[3]","Anz Schaltsp Alarm",197,1,"3","Bit","0x100","-","Meldung: Zu viele Schaltspiele. (Der Zählerstand »AuslBef Z« hat den unter »Anz Schaltsp Alarm« eingestellten Wert überschritten.)"]
["SG[3]","SGWartAlarm",197,1,"3","Bit","0x200","-","Meldung: Schwelle für den Revisions-Alarm"]
["SG[3]","SGWartVerrieg",197,1,"3","Bit","0x400","-","Meldung: Schwelle für die Verriegelung"]
["SG[3]","Sum Ik/h Alarm",197,1,"3","Bit","0x800","-","Meldung: Alarm, die Summe (kumuliert) der pro Stunde zulässigen Abschaltströme wurde überschritten."]
["SG[3]","Entnommen-E",258,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Leistungsschalter entnommen."]
["SG[3]","SBÜ SG entnommen",258,1,"3","Bit","0x2","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos, da Schaltgerät entnommen."]
["SG[3]","Entnommen",258,1,"3","Bit","0x4","-","Meldung: Leistungsschalter entnommen."]
["SG[4]","Hiko AUS-E",186,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52b)"]
["SG[4]","Hiko EIN-E",186,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52a)"]
["SG[4]","Bereit-E",186,1,"3","Bit","0x4","-","Zustand des Moduleingangs: LS bereit"]
["SG[4]","Sys-in-Sync-E",186,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Innerhalb der Synchronisierzeit muss dieses Signal anstehen, damit zugeschaltet wird. Anderfalls war der Schaltversuch erfolglos."]
["SG[4]","Verrieg AUS1-E",186,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[4]","Verrieg AUS2-E",186,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[4]","Verrieg AUS3-E",186,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[4]","Verrieg EIN1-E",186,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[4]","Verrieg EIN2-E",186,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[4]","Verrieg EIN3-E",186,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[4]","SBef AUS-E",186,1,"3","Bit","0x800","-","Zustand des Moduleingangs: Ausschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[4]","SBef EIN-E",186,1,"3","Bit","0x1000","-","Zustand des Moduleingangs: Einschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[4]","AuslBef (*)",186,1,"3","Bit","0x2000","-","Meldung: Auslösebefehl"]
["SG[4]","AUS Bef",186,1,"3","Bit","0x4000","-","Meldung: Ausschaltbefehl an das Schaltgerät. Dieser Ausschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze AUS-Kommando beinhalten."]
["SG[4]","AUS Bef manuell",186,1,"3","Bit","0x8000","-","Meldung: Manueller Ausschaltbefehl"]
["SG[4]","EIN Bef",187,1,"3","Bit","0x1","-","Meldung: Einschaltbefehl an das Schaltgerät. Dieser Einschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze EIN-Kommando beinhalten."]
["SG[4]","EIN Bef  manuell",187,1,"3","Bit","0x2","-","Meldung: Manueller Einschaltbefehl"]
["SG[4]","Sync EIN Anforderung",187,1,"3","Bit","0x4","-","Meldung: Anforderung synchronen Zuschaltens"]
["SG[4]","SGMon SGverzögert",187,1,"3","Bit","0x8","-","Meldung: Schaltgerätewartung: Alarm, der Schalter wird langsamer"]
["SG[4]","Res SGMon Sgverz",187,1,"3","Bit","0x10","-","Meldung: Rücksetzen der Meldung des verlangsamten Schalters"]
["SG[4]","SBÜ Störstellung",187,1,"3","Bit","0x40","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos. Schaltgerät in Störstellung."]
["SG[4]","SBÜ Feldverrieg",187,1,"3","Bit","0x80","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl verstößt gegen eine Feldverriegelung."]
["SG[4]","SBÜ EIN währd AUSBef",187,1,"3","Bit","0x400","-","Meldung: Schaltbefehlsüberwachung: Während ein Ausschaltbefehl aussteht, kommt ein Einschaltbefehl."]
["SG[4]","SBÜ Schaltrichtg",187,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung bzw Schaltrichtungsüberwachung: Dieses Signal wird wahr, wenn die Position, in der sich ein Schaltgerät befindet erneut angesteuert werden soll. Beispiel: Ein Schaltgerät, das sich bereits in der \"AUS\"-Position befindet, soll erneut \"AUS\"-geschaltet werden. Das Gleiche gilt für EIN-Kommandos."]
["SG[4]","SBÜ SG n. bereit",187,1,"3","Bit","0x1000","-","Meldung: Schaltbefehlsüberwachung: Das Schaltgerät ist nicht bereit."]
["SG[4]","SBÜ SyncTimeout",187,1,"3","Bit","0x2000","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl wurde nicht ausgeführt. Es wurde während der Synchronisierzeit kein Synchronisiersignal empfangen."]
["SG[4]","SBÜ erfolgreich",187,1,"3","Bit","0x4000","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolgreich"]
["SG[4]","Schutz EIN",187,1,"3","Bit","0x8000","-","Meldung: EIN Kommando durch das Schutzmodul"]
["SG[4]","Pos Gestört",188,1,"3","Bit","0x1","-","Meldung: Leistungsschalter Fehler - Unklare Schalterstellung. Die Stellungskontakte widersprechen  sich.  Nach Ablauf des Timers wird dieser Alarm ausgegeben."]
["SG[4]","t-Nachdrück",188,1,"3","Bit","0x2","-","Meldung: Nachdrückzeit"]
["SG[4]","Pos Unbest",188,1,"3","Bit","0x4","-","Meldung: Leistungsschalterstellung ist unbestimmt."]
["SG[4]","Pos AUS",188,1,"3","Bit","0x8","-","Meldung: Leistungsschalter ist in AUS-Position"]
["SG[4]","Pos EIN",188,1,"3","Bit","0x10","-","Meldung: Leistungsschalter ist in EIN-Position"]
["SG[4]","Bereit",188,1,"3","Bit","0x20","-","Meldung: Leistungsschalter ist schaltbereit."]
["SG[4]","Pos nicht EIN",188,1,"3","Bit","0x40","-","Meldung: Pos nicht EIN"]
["SG[4]","EKA Nur ein HIKO",188,1,"3","Bit","0x80","-","Meldung: Die Position des Schaltgeräts wird nur über einen einzelnen Hilfskontakt (Einpolige-Kontakt-Anzeige) erfasst. Zwischen- oder Störstellungen können auf diese Weise nicht erfasst werden."]
["SG[4]","Stellgsmeldg manipul",188,1,"3","Bit","0x100","-","Meldung: Stellungsmeldung manipuliert"]
["SG[4]","AUS inkl Schutz AUS",188,1,"3","Bit","0x200","-","Meldung: Das AUS-Kommando beinhaltet die durch den Schutz abgegebenen AUS-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[4]","EIN inkl Schutz EIN",188,1,"3","Bit","0x400","-","Meldung: Das EIN-Kommando beinhaltet die durch den Schutz abgegebenen EIN-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[4]","SBÜ Fehler AUSBef",188,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung: Wegen eines anstehenden Auslösebefehl wurde der Ausschaltbefehl nicht ausgeführt."]
["SG[4]","Verrieg AUS",188,1,"3","Bit","0x1000","-","Meldung: Mindestens ein AUS-Schaltbefehl ist verriegelt."]
["SG[4]","Verrieg EIN",188,1,"3","Bit","0x2000","-","Meldung: Mindestens ein EIN-Schaltbefehl ist verriegelt."]
["SG[4]","Sum Abschalt",198,1,"3","Bit","0x10","-","Meldung: Höchstzulässige Summe der Abschaltströme wurde in mindestens einer Phase überschritten"]
["SG[4]","Sum Abschalt:  IL1",198,1,"3","Bit","0x20","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL1"]
["SG[4]","Sum Abschalt:  IL2",198,1,"3","Bit","0x40","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL2"]
["SG[4]","Sum Abschalt:  IL3",198,1,"3","Bit","0x80","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL3"]
["SG[4]","Anz Schaltsp Alarm",198,1,"3","Bit","0x100","-","Meldung: Zu viele Schaltspiele. (Der Zählerstand »AuslBef Z« hat den unter »Anz Schaltsp Alarm« eingestellten Wert überschritten.)"]
["SG[4]","SGWartAlarm",198,1,"3","Bit","0x200","-","Meldung: Schwelle für den Revisions-Alarm"]
["SG[4]","SGWartVerrieg",198,1,"3","Bit","0x400","-","Meldung: Schwelle für die Verriegelung"]
["SG[4]","Sum Ik/h Alarm",198,1,"3","Bit","0x800","-","Meldung: Alarm, die Summe (kumuliert) der pro Stunde zulässigen Abschaltströme wurde überschritten."]
["SG[4]","Entnommen-E",259,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Leistungsschalter entnommen."]
["SG[4]","SBÜ SG entnommen",259,1,"3","Bit","0x2","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos, da Schaltgerät entnommen."]
["SG[4]","Entnommen",259,1,"3","Bit","0x4","-","Meldung: Leistungsschalter entnommen."]
["SG[5]","Hiko AUS-E",189,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52b)"]
["SG[5]","Hiko EIN-E",189,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52a)"]
["SG[5]","Bereit-E",189,1,"3","Bit","0x4","-","Zustand des Moduleingangs: LS bereit"]
["SG[5]","Sys-in-Sync-E",189,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Innerhalb der Synchronisierzeit muss dieses Signal anstehen, damit zugeschaltet wird. Anderfalls war der Schaltversuch erfolglos."]
["SG[5]","Verrieg AUS1-E",189,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[5]","Verrieg AUS2-E",189,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[5]","Verrieg AUS3-E",189,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[5]","Verrieg EIN1-E",189,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[5]","Verrieg EIN2-E",189,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[5]","Verrieg EIN3-E",189,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[5]","SBef AUS-E",189,1,"3","Bit","0x800","-","Zustand des Moduleingangs: Ausschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[5]","SBef EIN-E",189,1,"3","Bit","0x1000","-","Zustand des Moduleingangs: Einschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[5]","AuslBef (*)",189,1,"3","Bit","0x2000","-","Meldung: Auslösebefehl"]
["SG[5]","AUS Bef",189,1,"3","Bit","0x4000","-","Meldung: Ausschaltbefehl an das Schaltgerät. Dieser Ausschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze AUS-Kommando beinhalten."]
["SG[5]","AUS Bef manuell",189,1,"3","Bit","0x8000","-","Meldung: Manueller Ausschaltbefehl"]
["SG[5]","EIN Bef",190,1,"3","Bit","0x1","-","Meldung: Einschaltbefehl an das Schaltgerät. Dieser Einschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze EIN-Kommando beinhalten."]
["SG[5]","EIN Bef  manuell",190,1,"3","Bit","0x2","-","Meldung: Manueller Einschaltbefehl"]
["SG[5]","Sync EIN Anforderung",190,1,"3","Bit","0x4","-","Meldung: Anforderung synchronen Zuschaltens"]
["SG[5]","SGMon SGverzögert",190,1,"3","Bit","0x8","-","Meldung: Schaltgerätewartung: Alarm, der Schalter wird langsamer"]
["SG[5]","Res SGMon Sgverz",190,1,"3","Bit","0x10","-","Meldung: Rücksetzen der Meldung des verlangsamten Schalters"]
["SG[5]","SBÜ Störstellung",190,1,"3","Bit","0x40","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos. Schaltgerät in Störstellung."]
["SG[5]","SBÜ Feldverrieg",190,1,"3","Bit","0x80","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl verstößt gegen eine Feldverriegelung."]
["SG[5]","SBÜ EIN währd AUSBef",190,1,"3","Bit","0x400","-","Meldung: Schaltbefehlsüberwachung: Während ein Ausschaltbefehl aussteht, kommt ein Einschaltbefehl."]
["SG[5]","SBÜ Schaltrichtg",190,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung bzw Schaltrichtungsüberwachung: Dieses Signal wird wahr, wenn die Position, in der sich ein Schaltgerät befindet erneut angesteuert werden soll. Beispiel: Ein Schaltgerät, das sich bereits in der \"AUS\"-Position befindet, soll erneut \"AUS\"-geschaltet werden. Das Gleiche gilt für EIN-Kommandos."]
["SG[5]","SBÜ SG n. bereit",190,1,"3","Bit","0x1000","-","Meldung: Schaltbefehlsüberwachung: Das Schaltgerät ist nicht bereit."]
["SG[5]","SBÜ SyncTimeout",190,1,"3","Bit","0x2000","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl wurde nicht ausgeführt. Es wurde während der Synchronisierzeit kein Synchronisiersignal empfangen."]
["SG[5]","SBÜ erfolgreich",190,1,"3","Bit","0x4000","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolgreich"]
["SG[5]","Schutz EIN",190,1,"3","Bit","0x8000","-","Meldung: EIN Kommando durch das Schutzmodul"]
["SG[5]","Pos Gestört",191,1,"3","Bit","0x1","-","Meldung: Leistungsschalter Fehler - Unklare Schalterstellung. Die Stellungskontakte widersprechen  sich.  Nach Ablauf des Timers wird dieser Alarm ausgegeben."]
["SG[5]","t-Nachdrück",191,1,"3","Bit","0x2","-","Meldung: Nachdrückzeit"]
["SG[5]","Pos Unbest",191,1,"3","Bit","0x4","-","Meldung: Leistungsschalterstellung ist unbestimmt."]
["SG[5]","Pos AUS",191,1,"3","Bit","0x8","-","Meldung: Leistungsschalter ist in AUS-Position"]
["SG[5]","Pos EIN",191,1,"3","Bit","0x10","-","Meldung: Leistungsschalter ist in EIN-Position"]
["SG[5]","Bereit",191,1,"3","Bit","0x20","-","Meldung: Leistungsschalter ist schaltbereit."]
["SG[5]","Pos nicht EIN",191,1,"3","Bit","0x40","-","Meldung: Pos nicht EIN"]
["SG[5]","EKA Nur ein HIKO",191,1,"3","Bit","0x80","-","Meldung: Die Position des Schaltgeräts wird nur über einen einzelnen Hilfskontakt (Einpolige-Kontakt-Anzeige) erfasst. Zwischen- oder Störstellungen können auf diese Weise nicht erfasst werden."]
["SG[5]","Stellgsmeldg manipul",191,1,"3","Bit","0x100","-","Meldung: Stellungsmeldung manipuliert"]
["SG[5]","AUS inkl Schutz AUS",191,1,"3","Bit","0x200","-","Meldung: Das AUS-Kommando beinhaltet die durch den Schutz abgegebenen AUS-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[5]","EIN inkl Schutz EIN",191,1,"3","Bit","0x400","-","Meldung: Das EIN-Kommando beinhaltet die durch den Schutz abgegebenen EIN-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[5]","SBÜ Fehler AUSBef",191,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung: Wegen eines anstehenden Auslösebefehl wurde der Ausschaltbefehl nicht ausgeführt."]
["SG[5]","Verrieg AUS",191,1,"3","Bit","0x1000","-","Meldung: Mindestens ein AUS-Schaltbefehl ist verriegelt."]
["SG[5]","Verrieg EIN",191,1,"3","Bit","0x2000","-","Meldung: Mindestens ein EIN-Schaltbefehl ist verriegelt."]
["SG[5]","Sum Abschalt",199,1,"3","Bit","0x10","-","Meldung: Höchstzulässige Summe der Abschaltströme wurde in mindestens einer Phase überschritten"]
["SG[5]","Sum Abschalt:  IL1",199,1,"3","Bit","0x20","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL1"]
["SG[5]","Sum Abschalt:  IL2",199,1,"3","Bit","0x40","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL2"]
["SG[5]","Sum Abschalt:  IL3",199,1,"3","Bit","0x80","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL3"]
["SG[5]","Anz Schaltsp Alarm",199,1,"3","Bit","0x100","-","Meldung: Zu viele Schaltspiele. (Der Zählerstand »AuslBef Z« hat den unter »Anz Schaltsp Alarm« eingestellten Wert überschritten.)"]
["SG[5]","SGWartAlarm",199,1,"3","Bit","0x200","-","Meldung: Schwelle für den Revisions-Alarm"]
["SG[5]","SGWartVerrieg",199,1,"3","Bit","0x400","-","Meldung: Schwelle für die Verriegelung"]
["SG[5]","Sum Ik/h Alarm",199,1,"3","Bit","0x800","-","Meldung: Alarm, die Summe (kumuliert) der pro Stunde zulässigen Abschaltströme wurde überschritten."]
["SG[5]","Entnommen-E",260,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Leistungsschalter entnommen."]
["SG[5]","SBÜ SG entnommen",260,1,"3","Bit","0x2","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos, da Schaltgerät entnommen."]
["SG[5]","Entnommen",260,1,"3","Bit","0x4","-","Meldung: Leistungsschalter entnommen."]
["SG[6]","Hiko AUS-E",192,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52b)"]
["SG[6]","Hiko EIN-E",192,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Stellungsmeldung des Leistungsschalters (52a)"]
["SG[6]","Bereit-E",192,1,"3","Bit","0x4","-","Zustand des Moduleingangs: LS bereit"]
["SG[6]","Sys-in-Sync-E",192,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Innerhalb der Synchronisierzeit muss dieses Signal anstehen, damit zugeschaltet wird. Anderfalls war der Schaltversuch erfolglos."]
["SG[6]","Verrieg AUS1-E",192,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[6]","Verrieg AUS2-E",192,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[6]","Verrieg AUS3-E",192,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Verriegelung des  AUS-Schaltbefehls"]
["SG[6]","Verrieg EIN1-E",192,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[6]","Verrieg EIN2-E",192,1,"3","Bit","0x100","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[6]","Verrieg EIN3-E",192,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Verriegelung des  EIN-Schaltbefehls"]
["SG[6]","SBef AUS-E",192,1,"3","Bit","0x800","-","Zustand des Moduleingangs: Ausschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[6]","SBef EIN-E",192,1,"3","Bit","0x1000","-","Zustand des Moduleingangs: Einschaltbefehl, ggf Zustand der Logik oder des Digitalen Eingangs"]
["SG[6]","AuslBef (*)",192,1,"3","Bit","0x2000","-","Meldung: Auslösebefehl"]
["SG[6]","AUS Bef",192,1,"3","Bit","0x4000","-","Meldung: Ausschaltbefehl an das Schaltgerät. Dieser Ausschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze AUS-Kommando beinhalten."]
["SG[6]","AUS Bef manuell",192,1,"3","Bit","0x8000","-","Meldung: Manueller Ausschaltbefehl"]
["SG[6]","EIN Bef",193,1,"3","Bit","0x1","-","Meldung: Einschaltbefehl an das Schaltgerät. Dieser Einschaltbefehl kann je nach Parametrierung auch das vom Schutz abgesetze EIN-Kommando beinhalten."]
["SG[6]","EIN Bef  manuell",193,1,"3","Bit","0x2","-","Meldung: Manueller Einschaltbefehl"]
["SG[6]","Sync EIN Anforderung",193,1,"3","Bit","0x4","-","Meldung: Anforderung synchronen Zuschaltens"]
["SG[6]","SGMon SGverzögert",193,1,"3","Bit","0x8","-","Meldung: Schaltgerätewartung: Alarm, der Schalter wird langsamer"]
["SG[6]","Res SGMon Sgverz",193,1,"3","Bit","0x10","-","Meldung: Rücksetzen der Meldung des verlangsamten Schalters"]
["SG[6]","SBÜ Störstellung",193,1,"3","Bit","0x40","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos. Schaltgerät in Störstellung."]
["SG[6]","SBÜ Feldverrieg",193,1,"3","Bit","0x80","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl verstößt gegen eine Feldverriegelung."]
["SG[6]","SBÜ EIN währd AUSBef",193,1,"3","Bit","0x400","-","Meldung: Schaltbefehlsüberwachung: Während ein Ausschaltbefehl aussteht, kommt ein Einschaltbefehl."]
["SG[6]","SBÜ Schaltrichtg",193,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung bzw Schaltrichtungsüberwachung: Dieses Signal wird wahr, wenn die Position, in der sich ein Schaltgerät befindet erneut angesteuert werden soll. Beispiel: Ein Schaltgerät, das sich bereits in der \"AUS\"-Position befindet, soll erneut \"AUS\"-geschaltet werden. Das Gleiche gilt für EIN-Kommandos."]
["SG[6]","SBÜ SG n. bereit",193,1,"3","Bit","0x1000","-","Meldung: Schaltbefehlsüberwachung: Das Schaltgerät ist nicht bereit."]
["SG[6]","SBÜ SyncTimeout",193,1,"3","Bit","0x2000","-","Meldung: Schaltbefehlsüberwachung: Der Schaltbefehl wurde nicht ausgeführt. Es wurde während der Synchronisierzeit kein Synchronisiersignal empfangen."]
["SG[6]","SBÜ erfolgreich",193,1,"3","Bit","0x4000","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolgreich"]
["SG[6]","Schutz EIN",193,1,"3","Bit","0x8000","-","Meldung: EIN Kommando durch das Schutzmodul"]
["SG[6]","Pos Gestört",194,1,"3","Bit","0x1","-","Meldung: Leistungsschalter Fehler - Unklare Schalterstellung. Die Stellungskontakte widersprechen  sich.  Nach Ablauf des Timers wird dieser Alarm ausgegeben."]
["SG[6]","t-Nachdrück",194,1,"3","Bit","0x2","-","Meldung: Nachdrückzeit"]
["SG[6]","Pos Unbest",194,1,"3","Bit","0x4","-","Meldung: Leistungsschalterstellung ist unbestimmt."]
["SG[6]","Pos AUS",194,1,"3","Bit","0x8","-","Meldung: Leistungsschalter ist in AUS-Position"]
["SG[6]","Pos EIN",194,1,"3","Bit","0x10","-","Meldung: Leistungsschalter ist in EIN-Position"]
["SG[6]","Bereit",194,1,"3","Bit","0x20","-","Meldung: Leistungsschalter ist schaltbereit."]
["SG[6]","Pos nicht EIN",194,1,"3","Bit","0x40","-","Meldung: Pos nicht EIN"]
["SG[6]","EKA Nur ein HIKO",194,1,"3","Bit","0x80","-","Meldung: Die Position des Schaltgeräts wird nur über einen einzelnen Hilfskontakt (Einpolige-Kontakt-Anzeige) erfasst. Zwischen- oder Störstellungen können auf diese Weise nicht erfasst werden."]
["SG[6]","Stellgsmeldg manipul",194,1,"3","Bit","0x100","-","Meldung: Stellungsmeldung manipuliert"]
["SG[6]","AUS inkl Schutz AUS",194,1,"3","Bit","0x200","-","Meldung: Das AUS-Kommando beinhaltet die durch den Schutz abgegebenen AUS-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[6]","EIN inkl Schutz EIN",194,1,"3","Bit","0x400","-","Meldung: Das EIN-Kommando beinhaltet die durch den Schutz abgegebenen EIN-Kommandos (Es wird nur ein Ausgangsrelais benötigt)."]
["SG[6]","SBÜ Fehler AUSBef",194,1,"3","Bit","0x800","-","Meldung: Schaltbefehlsüberwachung: Wegen eines anstehenden Auslösebefehl wurde der Ausschaltbefehl nicht ausgeführt."]
["SG[6]","Verrieg AUS",194,1,"3","Bit","0x1000","-","Meldung: Mindestens ein AUS-Schaltbefehl ist verriegelt."]
["SG[6]","Verrieg EIN",194,1,"3","Bit","0x2000","-","Meldung: Mindestens ein EIN-Schaltbefehl ist verriegelt."]
["SG[6]","Sum Abschalt",201,1,"3","Bit","0x10","-","Meldung: Höchstzulässige Summe der Abschaltströme wurde in mindestens einer Phase überschritten"]
["SG[6]","Sum Abschalt:  IL1",201,1,"3","Bit","0x20","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL1"]
["SG[6]","Sum Abschalt:  IL2",201,1,"3","Bit","0x40","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL2"]
["SG[6]","Sum Abschalt:  IL3",201,1,"3","Bit","0x80","-","Meldung: Höchstzulässige Summe der Abschaltströme überschritten:  IL3"]
["SG[6]","Anz Schaltsp Alarm",201,1,"3","Bit","0x100","-","Meldung: Zu viele Schaltspiele. (Der Zählerstand »AuslBef Z« hat den unter »Anz Schaltsp Alarm« eingestellten Wert überschritten.)"]
["SG[6]","SGWartAlarm",201,1,"3","Bit","0x200","-","Meldung: Schwelle für den Revisions-Alarm"]
["SG[6]","SGWartVerrieg",201,1,"3","Bit","0x400","-","Meldung: Schwelle für die Verriegelung"]
["SG[6]","Sum Ik/h Alarm",201,1,"3","Bit","0x800","-","Meldung: Alarm, die Summe (kumuliert) der pro Stunde zulässigen Abschaltströme wurde überschritten."]
["SG[6]","Entnommen-E",261,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Leistungsschalter entnommen."]
["SG[6]","SBÜ SG entnommen",261,1,"3","Bit","0x2","-","Meldung: Schaltbefehlsüberwachung: Schaltbefehl war erfolglos, da Schaltgerät entnommen."]
["SG[6]","Entnommen",261,1,"3","Bit","0x4","-","Meldung: Leistungsschalter entnommen."]
["SPÜ","ExBlo1-E",81,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["SPÜ","ExBlo2-E",81,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["SPÜ","Aktiv",81,1,"3","Bit","0x4","-","Meldung: aktiv"]
["SPÜ","ExBlo",81,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["SPÜ","PoV Blo ",81,1,"3","Bit","0x10","-","Meldung: Loss of Potential  blockiert andere Module"]
["SPÜ","Alarm ",81,1,"3","Bit","0x20","-","Meldung: Alarm Loss of Potential"]
["SPÜ","Ex Automf. ESpW",81,1,"3","Bit","0x1000","-","Meldung:  Automatenfall Erdspannungswandler"]
["SPÜ","Ex Automf. SpW",81,1,"3","Bit","0x2000","-","Meldung: Ex Automf. SpW"]
["SPÜ","Ex Automf. ESpW-E",202,1,"3","Bit","0x1","-","Zustand des Moduleingangs:  Automatenfall Erdspannungswandler"]
["SPÜ","Ex Automf. SpW-E",202,1,"3","Bit","0x2","-","Zustand des Moduleingangs:  Automatenfall Spannungswandler"]
["SPÜ","Blo Trigger1-E",202,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Durch eine Anregung in dieser Schutzstufe, wird die Spannungswandlerfehlererkennung blockiert."]
["SPÜ","Blo Trigger2-E",202,1,"3","Bit","0x8","-","Zustand des Moduleingangs: Durch eine Anregung in dieser Schutzstufe, wird die Spannungswandlerfehlererkennung blockiert."]
["SPÜ","Blo Trigger3-E",202,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Durch eine Anregung in dieser Schutzstufe, wird die Spannungswandlerfehlererkennung blockiert."]
["SPÜ","Blo Trigger4-E",202,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Durch eine Anregung in dieser Schutzstufe, wird die Spannungswandlerfehlererkennung blockiert."]
["SPÜ","Blo Trigger5-E",202,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Durch eine Anregung in dieser Schutzstufe, wird die Spannungswandlerfehlererkennung blockiert."]
["Satz-Umschaltung","PS 1",59,1,"3","Bit","0x1","-","Meldung: Der aktive Parametersatz ist aktuell PS 1"]
["Satz-Umschaltung","PS 2",59,1,"3","Bit","0x2","-","Meldung: Der aktive Parametersatz ist aktuell PS 2"]
["Satz-Umschaltung","PS 3",59,1,"3","Bit","0x4","-","Meldung: Der aktive Parametersatz ist aktuell PS 3"]
["Satz-Umschaltung","PS 4",59,1,"3","Bit","0x8","-","Meldung: Der aktive Parametersatz ist aktuell PS 4"]
["Satz-Umschaltung","PSU manuell",59,1,"3","Bit","0x10","-","Meldung: Manuelle Umschaltung des Parametersatzes"]
["Satz-Umschaltung","PSU via Leittech",59,1,"3","Bit","0x20","-","Meldung: Parametersatz-Umschaltung über Leittechnik. Schreiben Sie in dieses Output-Byte den Integer-Wert des Parametersatzes, auf den geschaltet werden soll (z.B. 4 => Umschalten auf Parametersatz 4). "]
["Satz-Umschaltung","PSU via Eingsfkt",59,1,"3","Bit","0x40","-","Meldung: Parametersatz-Umschaltung über Eingangsfunktion"]
["Satz-Umschaltung","PS1-E",59,1,"3","Bit","0x80","-","Zustand des Moduleingangs bzw. des Signals, das diesen Parametersatz aktivieren soll."]
["Satz-Umschaltung","PS2-E",59,1,"3","Bit","0x100","-","Zustand des Moduleingangs bzw. des Signals, das diesen Parametersatz aktivieren soll."]
["Satz-Umschaltung","PS3-E",59,1,"3","Bit","0x200","-","Zustand des Moduleingangs bzw. des Signals, das diesen Parametersatz aktivieren soll."]
["Satz-Umschaltung","PS4-E",59,1,"3","Bit","0x400","-","Zustand des Moduleingangs bzw. des Signals, das diesen Parametersatz aktivieren soll."]
["Satz-Umschaltung","mind. 1 Param geänd. (*)",59,1,"3","Bit","0x800","-","Meldung: Mindestens ein Parameter wurde geändert"]
["Schutz","ExBlo1-E",1,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["Schutz","ExBlo2-E",1,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["Schutz","Aktiv",1,1,"3","Bit","0x4","-","Meldung: aktiv"]
["Schutz","ExBlo",1,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["Schutz","Alarm L1",1,1,"3","Bit","0x10","-","Meldung: General-Alarm L1"]
["Schutz","Alarm L2",1,1,"3","Bit","0x20","-","Meldung: General-Alarm L2"]
["Schutz","Alarm L3",1,1,"3","Bit","0x40","-","Meldung: General-Alarm L3"]
["Schutz","Alarm E",1,1,"3","Bit","0x80","-","Meldung: General-Alarm - Erdfehler"]
["Schutz","Alarm",1,1,"3","Bit","0x100","-","Meldung: General-Alarm"]
["Schutz","Ausl L1 (*)",1,1,"3","Bit","0x200","-","Meldung: General-Auslösung L1"]
["Schutz","Ausl L2 (*)",1,1,"3","Bit","0x400","-","Meldung: General-Auslösung L2"]
["Schutz","Ausl L3 (*)",1,1,"3","Bit","0x800","-","Meldung: General-Auslösung L3"]
["Schutz","Ausl E (*)",1,1,"3","Bit","0x1000","-","Meldung: General-Auslösung Erdfehler"]
["Schutz","Ausl (*)",1,1,"3","Bit","0x2000","-","Meldung: General-Auslösung"]
["Schutz","Blo AuslBef",2,1,"3","Bit","0x1","-","Meldung: Auslösebefehl blockiert"]
["Schutz","ExBlo AuslBef-E",2,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["Schutz","ExBlo AuslBef",2,1,"3","Bit","0x4","-","Meldung: Externe Blockade des Auslösekommandos"]
["Schutz","I Rch vorw",2,1,"3","Bit","0x80","-","Meldung: Phasenstromfehler vorwärts"]
["Schutz","I Rch rückw",2,1,"3","Bit","0x100","-","Meldung: Phasenstromfehler rückwärts"]
["Schutz","I Rch n mögl",2,1,"3","Bit","0x200","-","Meldung: Phasenfehler - fehlende Referenzspannung"]
["Schutz","Störfall-Nr.",57,1,"3","Bit","0xffff","-","Störfallnummer"]
["Schutz","Netzstör-Nr.",58,1,"3","Bit","0xffff","-","Netzstörungsnummer: Hier wird jeder Fehler, d.h. jede Generalanregung (Signal »Schutz . Alarm«) gezählt, jedoch nur dann, wenn nicht zugleich schon eine Wiedereinschaltung (Signal »AWE . läuft«) aktiv ist. (Anmerkung: Im Gegensatz hierzu zählt die »Störfall-Nr.« jeden Netzfehler, unabhängig von der Wiedereinschaltung. Für Schutzgeräte ohne AWE-Modul sind diese beiden Zähler prinzipiell gleichbedeutend.)"]
["Schutz","IE err Rch rückw",200,1,"3","Bit","0x1","-","Meldung: Erdstrom (errechnet) Fehler in Rückwärtsrichtung"]
["Schutz","IE err Rch vorw",200,1,"3","Bit","0x2","-","Meldung: Erdstrom (errechnet) Fehler in Vorwärtsrichtung"]
["Schutz","IE err Rch n mögl",200,1,"3","Bit","0x4","-","Meldung: Richtungsbestimmung des Erdtroms (errechnet) nicht möglich"]
["Schutz","IE gem  Rch rückw",200,1,"3","Bit","0x8","-","Meldung: Erdstrom (gemessen) Fehler in Rückwärtsrichtung"]
["Schutz","IE gem Rch vorw",200,1,"3","Bit","0x10","-","Meldung: Erdstrom (gemessen) Fehler in Vorwärtsrichtung"]
["Schutz","IE gem Rch n mögl",200,1,"3","Bit","0x20","-","Meldung: Richtungsbestimmung des Erdtroms (gemessen) nicht möglich"]
["Schutz","DFT ungültig",200,1,"3","Bit","0x40","-","Werte der DFT wie Grundwelle und Harmonische (alle bis auf UX) sind ungültig."]
["Schutz","f(UL123)>10Hz",200,1,"3","Bit","0x80","-","Frequenz der Meßkanäle 1-3(UL1,UL2,UL3) ist größer 10 Hz."]
["Schutz","f(UL123)>70Hz",200,1,"3","Bit","0x100","-","Frequenz der Meßkanäle 1-3(UL1,UL2,UL3) ist größer 70 Hz."]
["Schutz","f(UL123)<10Hz",200,1,"3","Bit","0x200","-","Frequenz der Meßkanäle 1-3(UL1,UL2,UL3) ist kleiner 10 Hz."]
["Schutz","f(UL123)<70Hz",200,1,"3","Bit","0x400","-","Frequenz der Meßkanäle 1-3(UL1,UL2,UL3) ist kleiner 70 Hz."]
["Schutz","DFT ungültig (UX)",200,1,"3","Bit","0x800","-","Werte der DFT wie Grundwelle und Harmonische von UX sind ungültig."]
["Schutz","f(UX)>10Hz",200,1,"3","Bit","0x1000","-","Frequenz des Messkanals 4(UX) ist größer 10 Hz."]
["Schutz","f(UX)>70Hz",200,1,"3","Bit","0x2000","-","Frequenz des Messkanals 4(UX) ist größer 70 Hz."]
["Schutz","f(UX)<10Hz",200,1,"3","Bit","0x4000","-","Frequenz des Messkanals 4(UX) ist kleiner 10 Hz."]
["Schutz","f(UX)<70Hz",200,1,"3","Bit","0x8000","-","Frequenz des Messkanals 4(UX) ist kleiner 70 Hz."]
["Sgen","ExBlo1-E",1012,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["Sgen","Ex ErzwingeNachl-E",1012,1,"3","Bit","0x2","-","Zustand des Moduleingangs:Erzwinge den Wechsel in die  Nachlaufphase. Abbruch der Simulation."]
["Sgen","läuft",1012,1,"3","Bit","0x10","-","Meldung: Messwertsimulation läuft"]
["Sgen","Status",1012,1,"3","Bit","0xe0","-","Meldung: Stati der Messwertsimulation :0=Off, 1=Fehlersimulation-Vorlauf, 2=Fehlersimulation, 3=Fehlersimulation-Nachlauf, 4=InitReset"]
["Sgen","Ex Start Simulation-E",1012,1,"3","Bit","0x100","-","Zustand des Moduleingangs:Externer Start der Fehler-Simulation (Verwendung der Test-Parameter)"]
["Sgen","ExBlo2-E",1012,1,"3","Bit","0x200","-","Zustand des Moduleingangs: Externe Blockade2"]
["Sgen","manuell gestartet",1012,1,"3","Bit","0x400","-","Fehler-Simulation wurde manuell gestartet"]
["Sgen","manuell gestoppt",1012,1,"3","Bit","0x800","-","Fehler-Simulation wurde manuell gestoppt"]
["Sgen","gestartet",1012,1,"3","Bit","0x1000","-","Fehler-Simulation hat gestartet"]
["Sgen","gestoppt",1012,1,"3","Bit","0x2000","-","Fehler-Simulation hat gestoppt"]
["StWÜ","ExBlo1-E",137,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["StWÜ","ExBlo2-E",137,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["StWÜ","Aktiv",137,1,"3","Bit","0x4","-","Meldung: aktiv"]
["StWÜ","ExBlo",137,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["StWÜ","Alarm",137,1,"3","Bit","0x10","-","Meldung: Alarm Stromwandlerüberwachung"]
["Strg","vor Ort",176,1,"3","Bit","0x1","-","Schalthoheit: Vor Ort"]
["Strg","Fern",176,1,"3","Bit","0x2","-","Schalthoheit: Fern"]
["Strg","Unverriegelt",176,1,"3","Bit","0x4","-","Unverrriegeltes Schalten ist aktiv"]
["Strg","SG Stör",176,1,"3","Bit","0x8","-","(Mindestens ein) Schaltgerät befindet sich in Störstellung."]
["Strg","SG Unbest",176,1,"3","Bit","0x10","-","(Mindestens ein) Schaltgerät ist in Bewegung (Position kann nicht eindeutig bestimmt werden)."]
["Sync","Aktiv",175,1,"3","Bit","0x1","-","Meldung: aktiv"]
["Sync","ExBlo1-E",175,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade1"]
["Sync","ExBlo2-E",175,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade2"]
["Sync","ExBlo",175,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["Sync","Durchsteuerung-E",175,1,"3","Bit","0x10","-","Zustand des Moduleingangs: Das Synchrocheckmodul wird überbrückt (durchgesteuert), wenn der Status des rangierten Signals wahr wird."]
["Sync","LSEinInit-E",175,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Initiierung des Einschaltens mit Synchrocheck aus beliebiger Quelle (z.B. Scada oder HMI). Wenn der Status des rangierten Signals wahr wird, wird die synchrone Einschaltung getriggert."]
["Sync","dWinkel >>",175,1,"3","Bit","0x40","-","Meldung: Phasendifferenzwinkel zwischen Sammelschiene und Netzspannung zu groß."]
["Sync","Sys-in-Sync",175,1,"3","Bit","0x80","-","Meldung: Sammelschienenspannung und Netzspannung sind synchron (gemäß den parametrierten Synchronitätsbedingungen)."]
["Sync","SS=Spg",175,1,"3","Bit","0x100","-","Meldung: Sammelschiene spannungsführend? \"1=spannungsführend\", \"0=Spannung liegt unterhalb der Schwelle für SS=Spg\"."]
["Sync","Netz=Spg",175,1,"3","Bit","0x200","-","Meldung: Netzseite spannungsführend? \"1=spannungsführend\", \"0=Spannung liegt unterhalb der Schwelle für Netz=Spg\"."]
["Sync","df >>",175,1,"3","Bit","0x400","-","Meldung: Frequenzunterschied (Schlupffrequenz) zwischen Sammelschiene und Netzspannung zu groß."]
["Sync","Durchsteuerung",175,1,"3","Bit","0x800","-","Meldung:Synchronisierüberwachung wird überbrückt (durchgesteuert). Eine der Überbrückungskriterien wurde erfüllt (Sammelschiene spannungslos, Netz ist spannungslos oder Überbrückungssignal)."]
["Sync","Zuschaltbereit",175,1,"3","Bit","0x1000","-","Meldung: Zuschaltbereit"]
["Sync","Störung",175,1,"3","Bit","0x2000","-","Meldung: Synchronisierung erfolglos. Befindet sich der Leistungsschalter nach Ablauf der höchstzulässigen Synchronisierzeit noch in der \"Offen-Position\", dann wird dieses Signal wird für 5 Sekunden ausgegeben."]
["Sync","läuft",175,1,"3","Bit","0x4000","-","Meldung: Synchronisiertimer läuft. Dieser Timer wird gestartet, wenn die Zuschaltung initiiert wird, und wird gestoppt, wenn der Leistungschalter eingeschaltet ist. Ein Timeout bedeutet, dass der Synchronisiervorgang erfolglos war."]
["Sync","dU >>",175,1,"3","Bit","0x8000","-","Meldung: Spannungsdifferenz zwischen Netz und Sammelschiene zu groß."]
["Sys","LichtbRed aktiv",154,1,"3","Bit","0x1","-","Meldung: Lichtbogenreduktion aktiv"]
["Sys","LichtbRed manuell",154,1,"3","Bit","0x2","-","Meldung: Lichtbogenreduktion Manueller Modus"]
["Sys","LichtbRed DI",154,1,"3","Bit","0x4","-","Meldung: Lichtbogenreduktion Modus Digitaler Eingang"]
["Sys","LichtbRed SCADA",154,1,"3","Bit","0x8","-","Meldung: Lichtbogenreduktion SCADA Modus"]
["Sys","LichtbRed inaktiv",154,1,"3","Bit","0x10","-","Meldung: Lichtbogenreduktion inaktiv"]
["Sys","LichtbRed-E",154,1,"3","Bit","0x20","-","Zustand des Moduleingangs: Lichtbogenreduktion bei Fehlern während Wartungsarbeiten"]
["Sys","Param-Verriegelung-E",154,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Solange dieser Eingang wahr ist, können keine Parameter geändert werden. Die Parametrierung ist verriegelt."]
["Sys","SNTP aktiv",154,1,"3","Bit","0x80","-","Meldung: Wenn für 120 s kein gültiges SNTP Signal vorhanden ist, dann wird SNTP als inaktiv angesehen."]
["Sys","Param Verrieg Bypass",154,1,"3","Bit","0x100","-","Meldung: Kurzzeitige Aufhebung der Parametriersperre"]
["SysA","ExBlo-E",173,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade"]
["SysA","ExBlo",173,1,"3","Bit","0x2","-","Meldung: Externe Blockade"]
["SysA","Alarm I mit (Bezug)",173,1,"3","Bit","0x4","-","Meldung: Alarm: Gemittelter Bezugsstrom zu hoch"]
["SysA","Aktiv",173,1,"3","Bit","0x8","-","Meldung: aktiv"]
["SysA","Alarm I THD",173,1,"3","Bit","0x10","-","Meldung: Alarm Verzerrungsstrom - Total Harmonic Distortion"]
["SysA","Alarm S Max (Bezug)",173,1,"3","Bit","0x20","-","Meldung: Alarm: Höchstzulässige Scheinleistung überschritten"]
["SysA","Alarm S mit (Bezug)",173,1,"3","Bit","0x40","-","Meldung: Alarm: Gemittelte Scheinleistung zu hoch"]
["SysA","Alarm Q Max (Bezug)",173,1,"3","Bit","0x80","-","Meldung: Alarm: Höchstzulässige Blindleistung überschritten"]
["SysA","Alarm Q mit (Bezug)",173,1,"3","Bit","0x100","-","Meldung: Alarm: Gemittelte Blindleistung zu hoch"]
["SysA","Alarm V THD",173,1,"3","Bit","0x200","-","Meldung: Alarm Spannungsverzerrung - Total Harmonic Distortion"]
["SysA","Alarm P Max (Bezug)",173,1,"3","Bit","0x400","-","Meldung: Alarm: Höchstzulässige Wirkleistung überschritten"]
["SysA","Alarm P mit (Bezug)",173,1,"3","Bit","0x800","-","Meldung: Alarm: Gemittelte Wirkleistung zu hoch"]
["SysA","Ausl Strom mit (Bezug) (*)",173,1,"3","Bit","0x1000","-","Meldung: Auslösung: Gemittelter Strombezug zu hoch"]
["SysA","Ausl I THD (*)",173,1,"3","Bit","0x2000","-","Meldung: Auslösung Verzerrungsstrom - Total Harmonic Distortion"]
["SysA","Ausl S mit (Bezug) (*)",173,1,"3","Bit","0x4000","-","Meldung: Auslösung: Gemittelter Scheinleistungsbezug zu hoch"]
["SysA","Ausl S Max (Bezug) (*)",173,1,"3","Bit","0x8000","-","Meldung: Auslösung, da höchstzulässige Scheinleistung überschritten"]
["SysA","Ausl Q mit (Bezug) (*)",174,1,"3","Bit","0x1","-","Meldung: Auslösung: Gemittelter Blindleistungsbezug zu hoch"]
["SysA","Ausl Q Max (Bezug) (*)",174,1,"3","Bit","0x2","-","Meldung: Auslösung, da höchstzulässige Blindleistung überschritten"]
["SysA","Ausl U THD (*)",174,1,"3","Bit","0x4","-","Meldung: Auslösung Spannungsverzerrung - Total Harmonic Distortion"]
["SysA","Ausl P mit (Bezug) (*)",174,1,"3","Bit","0x8","-","Meldung: Auslösung: Gemittelter Wirkleistungsbezug zu hoch"]
["SysA","Ausl P Max (Bezug) (*)",174,1,"3","Bit","0x10","-","Meldung: Auslösung, da höchstzulässige Wirkleistung überschritten"]
["SÜW","Systemfehler",273,1,"3","Bit","0x1","-","Meldung: Gerätefehler"]
["SÜW","Neuer Fehler (*)",273,1,"3","Bit","0x8","-","Meldung: Ein neuer Fehler wurde gemeldet."]
["SÜW","Neue Warnung (*)",273,1,"3","Bit","0x10","-","Meldung: Eine neue Warnung wurde gemeldet."]
["SÜW","Aktiv",273,1,"3","Bit","0x20","-","Meldung: aktiv"]
["ThA","ExBlo1-E",19,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["ThA","ExBlo2-E",19,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["ThA","ExBlo AuslBef-E",19,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["ThA","Aktiv",19,1,"3","Bit","0x8","-","Meldung: aktiv"]
["ThA","ExBlo",19,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["ThA","Blo AuslBef",19,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["ThA","ExBlo AuslBef",19,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["ThA","Alarm",19,1,"3","Bit","0x80","-","Meldung: Alarm Thermische Überlast"]
["ThA","Ausl (*)",19,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["ThA","AuslBef (*)",19,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["U012[1]","ExBlo1-E",100,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U012[1]","ExBlo2-E",100,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U012[1]","ExBlo AuslBef-E",100,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U012[1]","Aktiv",100,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U012[1]","ExBlo",100,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U012[1]","Blo AuslBef",100,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U012[1]","ExBlo AuslBef",100,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U012[1]","Alarm",100,1,"3","Bit","0x80","-","Meldung: Alarm Spannungsasymmetrie"]
["U012[1]","Ausl (*)",100,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["U012[1]","AuslBef (*)",100,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["U012[2]","ExBlo1-E",101,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U012[2]","ExBlo2-E",101,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U012[2]","ExBlo AuslBef-E",101,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U012[2]","Aktiv",101,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U012[2]","ExBlo",101,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U012[2]","Blo AuslBef",101,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U012[2]","ExBlo AuslBef",101,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U012[2]","Alarm",101,1,"3","Bit","0x80","-","Meldung: Alarm Spannungsasymmetrie"]
["U012[2]","Ausl (*)",101,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["U012[2]","AuslBef (*)",101,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["U012[3]","ExBlo1-E",102,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U012[3]","ExBlo2-E",102,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U012[3]","ExBlo AuslBef-E",102,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U012[3]","Aktiv",102,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U012[3]","ExBlo",102,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U012[3]","Blo AuslBef",102,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U012[3]","ExBlo AuslBef",102,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U012[3]","Alarm",102,1,"3","Bit","0x80","-","Meldung: Alarm Spannungsasymmetrie"]
["U012[3]","Ausl (*)",102,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["U012[3]","AuslBef (*)",102,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["U012[4]","ExBlo1-E",103,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U012[4]","ExBlo2-E",103,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U012[4]","ExBlo AuslBef-E",103,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U012[4]","Aktiv",103,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U012[4]","ExBlo",103,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U012[4]","Blo AuslBef",103,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U012[4]","ExBlo AuslBef",103,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U012[4]","Alarm",103,1,"3","Bit","0x80","-","Meldung: Alarm Spannungsasymmetrie"]
["U012[4]","Ausl (*)",103,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["U012[4]","AuslBef (*)",103,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["U012[5]","ExBlo1-E",104,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U012[5]","ExBlo2-E",104,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U012[5]","ExBlo AuslBef-E",104,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U012[5]","Aktiv",104,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U012[5]","ExBlo",104,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U012[5]","Blo AuslBef",104,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U012[5]","ExBlo AuslBef",104,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U012[5]","Alarm",104,1,"3","Bit","0x80","-","Meldung: Alarm Spannungsasymmetrie"]
["U012[5]","Ausl (*)",104,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["U012[5]","AuslBef (*)",104,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["U012[6]","ExBlo1-E",105,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U012[6]","ExBlo2-E",105,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U012[6]","ExBlo AuslBef-E",105,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U012[6]","Aktiv",105,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U012[6]","ExBlo",105,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U012[6]","Blo AuslBef",105,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U012[6]","ExBlo AuslBef",105,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U012[6]","Alarm",105,1,"3","Bit","0x80","-","Meldung: Alarm Spannungsasymmetrie"]
["U012[6]","Ausl (*)",105,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["U012[6]","AuslBef (*)",105,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["UE[1]","ExBlo1-E",32,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["UE[1]","ExBlo2-E",32,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["UE[1]","ExBlo AuslBef-E",32,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["UE[1]","Aktiv",32,1,"3","Bit","0x8","-","Meldung: aktiv"]
["UE[1]","ExBlo",32,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["UE[1]","Blo AuslBef",32,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["UE[1]","ExBlo AuslBef",32,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["UE[1]","Alarm",32,1,"3","Bit","0x80","-","Meldung: Alarm Verlagerungsspannungs-Stufe"]
["UE[1]","Ausl (*)",32,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["UE[1]","AuslBef (*)",32,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["UE[2]","ExBlo1-E",33,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["UE[2]","ExBlo2-E",33,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["UE[2]","ExBlo AuslBef-E",33,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["UE[2]","Aktiv",33,1,"3","Bit","0x8","-","Meldung: aktiv"]
["UE[2]","ExBlo",33,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["UE[2]","Blo AuslBef",33,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["UE[2]","ExBlo AuslBef",33,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["UE[2]","Alarm",33,1,"3","Bit","0x80","-","Meldung: Alarm Verlagerungsspannungs-Stufe"]
["UE[2]","Ausl (*)",33,1,"3","Bit","0x100","-","Meldung: Auslösung"]
["UE[2]","AuslBef (*)",33,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["UFLA","ExBlo1-E",272,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["UFLA","ExBlo2-E",272,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["UFLA","Ex P-Rtg-E",272,1,"3","Bit","0x4","-","Ignoriere (blockiere) die Auswertung der Richtung des Wirkleistungsflusses. Ist diese Funktionalität parametriert und aktiv, verändert sich die Funktionalität des Moduls hin zu konventionellem, rein frequenzabhängigen Lastabwurf."]
["UFLA","Aktiv",272,1,"3","Bit","0x8","-","Meldung: aktiv"]
["UFLA","ExBlo",272,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["UFLA","Autom Spw Blo",272,1,"3","Bit","0x20","-","Meldung: Blockade durch Spannungswandlerfehler (Automatenfall)"]
["UFLA","Ausl",272,1,"3","Bit","0x40","-","Meldung: Meldung: Auslösung"]
["UFLA","Alarm",272,1,"3","Bit","0x80","-","Meldung: Alarm UFLA"]
["U[1]","ExBlo1-E",24,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U[1]","ExBlo2-E",24,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U[1]","ExBlo AuslBef-E",24,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U[1]","Aktiv",24,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U[1]","ExBlo",24,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U[1]","Blo AuslBef",24,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U[1]","ExBlo AuslBef",24,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U[1]","Alarm L1",25,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["U[1]","Alarm L2",25,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["U[1]","Alarm L3",25,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["U[1]","Alarm",25,1,"3","Bit","0x8","-","Meldung: Alarm Spannungsstufe"]
["U[1]","Ausl L1 (*)",25,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["U[1]","Ausl L2 (*)",25,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["U[1]","Ausl L3 (*)",25,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["U[1]","Ausl (*)",25,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["U[1]","AuslBef (*)",25,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["U[1]","Imin-Freigabe aktiv",25,1,"3","Bit","0x200","-","Meldung, dass die Imin-Freigabeprüfung aktiv ist und die Unterspannungserkennung (momentan) nicht blockiert."]
["U[2]","ExBlo1-E",26,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U[2]","ExBlo2-E",26,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U[2]","ExBlo AuslBef-E",26,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U[2]","Aktiv",26,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U[2]","ExBlo",26,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U[2]","Blo AuslBef",26,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U[2]","ExBlo AuslBef",26,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U[2]","Alarm L1",27,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["U[2]","Alarm L2",27,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["U[2]","Alarm L3",27,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["U[2]","Alarm",27,1,"3","Bit","0x8","-","Meldung: Alarm Spannungsstufe"]
["U[2]","Ausl L1 (*)",27,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["U[2]","Ausl L2 (*)",27,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["U[2]","Ausl L3 (*)",27,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["U[2]","Ausl (*)",27,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["U[2]","AuslBef (*)",27,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["U[2]","Imin-Freigabe aktiv",27,1,"3","Bit","0x200","-","Meldung, dass die Imin-Freigabeprüfung aktiv ist und die Unterspannungserkennung (momentan) nicht blockiert."]
["U[3]","ExBlo1-E",28,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U[3]","ExBlo2-E",28,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U[3]","ExBlo AuslBef-E",28,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U[3]","Aktiv",28,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U[3]","ExBlo",28,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U[3]","Blo AuslBef",28,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U[3]","ExBlo AuslBef",28,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U[3]","Alarm L1",29,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["U[3]","Alarm L2",29,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["U[3]","Alarm L3",29,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["U[3]","Alarm",29,1,"3","Bit","0x8","-","Meldung: Alarm Spannungsstufe"]
["U[3]","Ausl L1 (*)",29,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["U[3]","Ausl L2 (*)",29,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["U[3]","Ausl L3 (*)",29,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["U[3]","Ausl (*)",29,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["U[3]","AuslBef (*)",29,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["U[3]","Imin-Freigabe aktiv",29,1,"3","Bit","0x200","-","Meldung, dass die Imin-Freigabeprüfung aktiv ist und die Unterspannungserkennung (momentan) nicht blockiert."]
["U[4]","ExBlo1-E",30,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U[4]","ExBlo2-E",30,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U[4]","ExBlo AuslBef-E",30,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U[4]","Aktiv",30,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U[4]","ExBlo",30,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U[4]","Blo AuslBef",30,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U[4]","ExBlo AuslBef",30,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U[4]","Alarm L1",31,1,"3","Bit","0x1","-","Meldung: Alarm L1"]
["U[4]","Alarm L2",31,1,"3","Bit","0x2","-","Meldung: Alarm L2"]
["U[4]","Alarm L3",31,1,"3","Bit","0x4","-","Meldung: Alarm L3"]
["U[4]","Alarm",31,1,"3","Bit","0x8","-","Meldung: Alarm Spannungsstufe"]
["U[4]","Ausl L1 (*)",31,1,"3","Bit","0x10","-","Meldung: General-Auslösung L1"]
["U[4]","Ausl L2 (*)",31,1,"3","Bit","0x20","-","Meldung: General-Auslösung L2"]
["U[4]","Ausl L3 (*)",31,1,"3","Bit","0x40","-","Meldung: General-Auslösung L3"]
["U[4]","Ausl (*)",31,1,"3","Bit","0x80","-","Meldung: Auslösung"]
["U[4]","AuslBef (*)",31,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["U[4]","Imin-Freigabe aktiv",31,1,"3","Bit","0x200","-","Meldung, dass die Imin-Freigabeprüfung aktiv ist und die Unterspannungserkennung (momentan) nicht blockiert."]
["U[5]","ExBlo1-E",92,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U[5]","ExBlo2-E",92,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U[5]","ExBlo AuslBef-E",92,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U[5]","Aktiv",92,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U[5]","ExBlo",92,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U[5]","Blo AuslBef",92,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U[5]","ExBlo AuslBef",92,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U[5]","Alarm",92,1,"3","Bit","0x80","-","Meldung: Alarm Spannungsstufe"]
["U[5]","Alarm L1",92,1,"3","Bit","0x100","-","Meldung: Alarm L1"]
["U[5]","Alarm L2",92,1,"3","Bit","0x200","-","Meldung: Alarm L2"]
["U[5]","Alarm L3",92,1,"3","Bit","0x400","-","Meldung: Alarm L3"]
["U[5]","Ausl (*)",92,1,"3","Bit","0x800","-","Meldung: Auslösung"]
["U[5]","Ausl L1 (*)",92,1,"3","Bit","0x1000","-","Meldung: General-Auslösung L1"]
["U[5]","Ausl L2 (*)",92,1,"3","Bit","0x2000","-","Meldung: General-Auslösung L2"]
["U[5]","Ausl L3 (*)",92,1,"3","Bit","0x4000","-","Meldung: General-Auslösung L3"]
["U[5]","AuslBef (*)",92,1,"3","Bit","0x8000","-","Meldung: Auslösebefehl"]
["U[5]","Imin-Freigabe aktiv",94,1,"3","Bit","0x1","-","Meldung, dass die Imin-Freigabeprüfung aktiv ist und die Unterspannungserkennung (momentan) nicht blockiert."]
["U[6]","ExBlo1-E",93,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["U[6]","ExBlo2-E",93,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["U[6]","ExBlo AuslBef-E",93,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["U[6]","Aktiv",93,1,"3","Bit","0x8","-","Meldung: aktiv"]
["U[6]","ExBlo",93,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["U[6]","Blo AuslBef",93,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["U[6]","ExBlo AuslBef",93,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["U[6]","Alarm",93,1,"3","Bit","0x80","-","Meldung: Alarm Spannungsstufe"]
["U[6]","Alarm L1",93,1,"3","Bit","0x100","-","Meldung: Alarm L1"]
["U[6]","Alarm L2",93,1,"3","Bit","0x200","-","Meldung: Alarm L2"]
["U[6]","Alarm L3",93,1,"3","Bit","0x400","-","Meldung: Alarm L3"]
["U[6]","Ausl (*)",93,1,"3","Bit","0x800","-","Meldung: Auslösung"]
["U[6]","Ausl L1 (*)",93,1,"3","Bit","0x1000","-","Meldung: General-Auslösung L1"]
["U[6]","Ausl L2 (*)",93,1,"3","Bit","0x2000","-","Meldung: General-Auslösung L2"]
["U[6]","Ausl L3 (*)",93,1,"3","Bit","0x4000","-","Meldung: General-Auslösung L3"]
["U[6]","AuslBef (*)",93,1,"3","Bit","0x8000","-","Meldung: Auslösebefehl"]
["U[6]","Imin-Freigabe aktiv",95,1,"3","Bit","0x1","-","Meldung, dass die Imin-Freigabeprüfung aktiv ist und die Unterspannungserkennung (momentan) nicht blockiert."]
["WZS[1]","ExBlo1-E",158,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["WZS[1]","ExBlo2-E",158,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["WZS[1]","Aktiv",158,1,"3","Bit","0x4","-","Meldung: aktiv"]
["WZS[1]","ExBlo",158,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["WZS[1]","Blo d. Messkreisüb.",158,1,"3","Bit","0x10","-","Meldung: Blockade des Moduls durch die Messkreisüberwachung "]
["WZS[1]","wieder zugeschaltet -E",158,1,"3","Bit","0x20","-","Durch diese Rangierung wird der Status \"wiederzugeschaltet\" (netzparallel) indiziert."]
["WZS[1]","U Ext Freigabe NAP-E",158,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Freigabesignal vom NAP (Externe Freigabe)."]
["WZS[1]","NAP Autom Spw-E",158,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Blockade bei erkanntem externem Automatenfall, falls die Freigabe von extern kommen soll."]
["WZS[1]","Freig.Wiederzusch.EZE",158,1,"3","Bit","0x100","-","Meldung: Meldung: Freigabe Erzeugungseinheit."]
["WZS[1]","Entkupplung1-E",158,1,"3","Bit","0x200","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[1]","Entkupplung2-E",158,1,"3","Bit","0x400","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[1]","Entkupplung3-E",158,1,"3","Bit","0x800","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[1]","Entkupplung4-E",158,1,"3","Bit","0x1000","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[1]","Entkupplung5-E",158,1,"3","Bit","0x2000","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[1]","Entkupplung6-E",158,1,"3","Bit","0x4000","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[2]","ExBlo1-E",159,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["WZS[2]","ExBlo2-E",159,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["WZS[2]","Aktiv",159,1,"3","Bit","0x4","-","Meldung: aktiv"]
["WZS[2]","ExBlo",159,1,"3","Bit","0x8","-","Meldung: Externe Blockade"]
["WZS[2]","Blo d. Messkreisüb.",159,1,"3","Bit","0x10","-","Meldung: Blockade des Moduls durch die Messkreisüberwachung "]
["WZS[2]","wieder zugeschaltet -E",159,1,"3","Bit","0x20","-","Durch diese Rangierung wird der Status \"wiederzugeschaltet\" (netzparallel) indiziert."]
["WZS[2]","U Ext Freigabe NAP-E",159,1,"3","Bit","0x40","-","Zustand des Moduleingangs: Freigabesignal vom NAP (Externe Freigabe)."]
["WZS[2]","NAP Autom Spw-E",159,1,"3","Bit","0x80","-","Zustand des Moduleingangs: Blockade bei erkanntem externem Automatenfall, falls die Freigabe von extern kommen soll."]
["WZS[2]","Freig.Wiederzusch.EZE",159,1,"3","Bit","0x100","-","Meldung: Meldung: Freigabe Erzeugungseinheit."]
["WZS[2]","Entkupplung1-E",159,1,"3","Bit","0x200","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[2]","Entkupplung2-E",159,1,"3","Bit","0x400","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[2]","Entkupplung3-E",159,1,"3","Bit","0x800","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[2]","Entkupplung4-E",159,1,"3","Bit","0x1000","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[2]","Entkupplung5-E",159,1,"3","Bit","0x2000","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["WZS[2]","Entkupplung6-E",159,1,"3","Bit","0x4000","-","Entkupplungsfunktion, die die Wiederzuschaltung triggert."]
["ZeitSync","Synchronisiert",54,1,"3","Bit","0x1","-","Uhrzeit ist synchonisiert."]
["delta phi","ExBlo1-E",249,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["delta phi","ExBlo2-E",249,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["delta phi","ExBlo AuslBef-E",249,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["delta phi","Aktiv",249,1,"3","Bit","0x8","-","Meldung: aktiv"]
["delta phi","ExBlo",249,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["delta phi","Blo AuslBef",249,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["delta phi","ExBlo AuslBef",249,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["delta phi","Alarm",249,1,"3","Bit","0x80","-","Meldung: Alarm Frequenzschutz (Sammelmeldung)"]
["delta phi","Ausl (*)",249,1,"3","Bit","0x100","-","Meldung: Auslösung Frequenzschutz (Sammelmeldung)"]
["delta phi","AuslBef (*)",249,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["delta phi","Blo durch U<",249,1,"3","Bit","0x400","-","Meldung: Modul wird durch Unterspannung blockiert."]
["df/dt","ExBlo1-E",250,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["df/dt","ExBlo2-E",250,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["df/dt","ExBlo AuslBef-E",250,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["df/dt","Aktiv",250,1,"3","Bit","0x8","-","Meldung: aktiv"]
["df/dt","ExBlo",250,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["df/dt","Blo AuslBef",250,1,"3","Bit","0x20","-","Meldung: Auslösebefehl blockiert"]
["df/dt","ExBlo AuslBef",250,1,"3","Bit","0x40","-","Meldung: Externe Blockade des Auslösekommandos"]
["df/dt","Alarm",250,1,"3","Bit","0x80","-","Meldung: Alarm Frequenzschutz (Sammelmeldung)"]
["df/dt","Ausl (*)",250,1,"3","Bit","0x100","-","Meldung: Auslösung Frequenzschutz (Sammelmeldung)"]
["df/dt","AuslBef (*)",250,1,"3","Bit","0x200","-","Meldung: Auslösebefehl"]
["df/dt","Blo durch U<",250,1,"3","Bit","0x400","-","Meldung: Modul wird durch Unterspannung blockiert."]
["f[1]","ExBlo1-E",34,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["f[1]","ExBlo2-E",34,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["f[1]","ExBlo AuslBef-E",34,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["f[1]","Aktiv",34,1,"3","Bit","0x8","-","Meldung: aktiv"]
["f[1]","ExBlo",34,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["f[1]","Blo durch U<",34,1,"3","Bit","0x20","-","Meldung: Modul wird durch Unterspannung blockiert."]
["f[1]","Blo AuslBef",34,1,"3","Bit","0x40","-","Meldung: Auslösebefehl blockiert"]
["f[1]","ExBlo AuslBef",34,1,"3","Bit","0x80","-","Meldung: Externe Blockade des Auslösekommandos"]
["f[1]","Alarm f",35,1,"3","Bit","0x1","-","Meldung: Alarm Frequenzschutz"]
["f[1]","Alarm df/dt | DF/DT",35,1,"3","Bit","0x2","-","Alarm momentane oder mittlere Frequenzänderungsgeschwindigkeit."]
["f[1]","Ausl f (*)",35,1,"3","Bit","0x4","-","Meldung: Auslösung, Frequenz hat zulässigen Grenzwert verletzt"]
["f[1]","Ausl df/dt | DF/DT (*)",35,1,"3","Bit","0x8","-","Meldung: Auslösung df/dt oder DF/DT"]
["f[1]","Alarm",35,1,"3","Bit","0x10","-","Meldung: Alarm Frequenzschutz (Sammelmeldung)"]
["f[1]","Alarm delta phi",35,1,"3","Bit","0x20","-","Meldung: Alarm Vektorsprung"]
["f[1]","Ausl (*)",35,1,"3","Bit","0x40","-","Meldung: Auslösung Frequenzschutz (Sammelmeldung)"]
["f[1]","Ausl delta phi (*)",35,1,"3","Bit","0x80","-","Meldung: Auslösung delta phi"]
["f[1]","AuslBef (*)",35,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["f[2]","ExBlo1-E",36,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["f[2]","ExBlo2-E",36,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["f[2]","ExBlo AuslBef-E",36,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["f[2]","Aktiv",36,1,"3","Bit","0x8","-","Meldung: aktiv"]
["f[2]","ExBlo",36,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["f[2]","Blo durch U<",36,1,"3","Bit","0x20","-","Meldung: Modul wird durch Unterspannung blockiert."]
["f[2]","Blo AuslBef",36,1,"3","Bit","0x40","-","Meldung: Auslösebefehl blockiert"]
["f[2]","ExBlo AuslBef",36,1,"3","Bit","0x80","-","Meldung: Externe Blockade des Auslösekommandos"]
["f[2]","Alarm f",37,1,"3","Bit","0x1","-","Meldung: Alarm Frequenzschutz"]
["f[2]","Alarm df/dt | DF/DT",37,1,"3","Bit","0x2","-","Alarm momentane oder mittlere Frequenzänderungsgeschwindigkeit."]
["f[2]","Ausl f (*)",37,1,"3","Bit","0x4","-","Meldung: Auslösung, Frequenz hat zulässigen Grenzwert verletzt"]
["f[2]","Ausl df/dt | DF/DT (*)",37,1,"3","Bit","0x8","-","Meldung: Auslösung df/dt oder DF/DT"]
["f[2]","Alarm",37,1,"3","Bit","0x10","-","Meldung: Alarm Frequenzschutz (Sammelmeldung)"]
["f[2]","Alarm delta phi",37,1,"3","Bit","0x20","-","Meldung: Alarm Vektorsprung"]
["f[2]","Ausl (*)",37,1,"3","Bit","0x40","-","Meldung: Auslösung Frequenzschutz (Sammelmeldung)"]
["f[2]","Ausl delta phi (*)",37,1,"3","Bit","0x80","-","Meldung: Auslösung delta phi"]
["f[2]","AuslBef (*)",37,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["f[3]","ExBlo1-E",38,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["f[3]","ExBlo2-E",38,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["f[3]","ExBlo AuslBef-E",38,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["f[3]","Aktiv",38,1,"3","Bit","0x8","-","Meldung: aktiv"]
["f[3]","ExBlo",38,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["f[3]","Blo durch U<",38,1,"3","Bit","0x20","-","Meldung: Modul wird durch Unterspannung blockiert."]
["f[3]","Blo AuslBef",38,1,"3","Bit","0x40","-","Meldung: Auslösebefehl blockiert"]
["f[3]","ExBlo AuslBef",38,1,"3","Bit","0x80","-","Meldung: Externe Blockade des Auslösekommandos"]
["f[3]","Alarm f",39,1,"3","Bit","0x1","-","Meldung: Alarm Frequenzschutz"]
["f[3]","Alarm df/dt | DF/DT",39,1,"3","Bit","0x2","-","Alarm momentane oder mittlere Frequenzänderungsgeschwindigkeit."]
["f[3]","Ausl f (*)",39,1,"3","Bit","0x4","-","Meldung: Auslösung, Frequenz hat zulässigen Grenzwert verletzt"]
["f[3]","Ausl df/dt | DF/DT (*)",39,1,"3","Bit","0x8","-","Meldung: Auslösung df/dt oder DF/DT"]
["f[3]","Alarm",39,1,"3","Bit","0x10","-","Meldung: Alarm Frequenzschutz (Sammelmeldung)"]
["f[3]","Alarm delta phi",39,1,"3","Bit","0x20","-","Meldung: Alarm Vektorsprung"]
["f[3]","Ausl (*)",39,1,"3","Bit","0x40","-","Meldung: Auslösung Frequenzschutz (Sammelmeldung)"]
["f[3]","Ausl delta phi (*)",39,1,"3","Bit","0x80","-","Meldung: Auslösung delta phi"]
["f[3]","AuslBef (*)",39,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["f[4]","ExBlo1-E",40,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["f[4]","ExBlo2-E",40,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["f[4]","ExBlo AuslBef-E",40,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["f[4]","Aktiv",40,1,"3","Bit","0x8","-","Meldung: aktiv"]
["f[4]","ExBlo",40,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["f[4]","Blo durch U<",40,1,"3","Bit","0x20","-","Meldung: Modul wird durch Unterspannung blockiert."]
["f[4]","Blo AuslBef",40,1,"3","Bit","0x40","-","Meldung: Auslösebefehl blockiert"]
["f[4]","ExBlo AuslBef",40,1,"3","Bit","0x80","-","Meldung: Externe Blockade des Auslösekommandos"]
["f[4]","Alarm f",41,1,"3","Bit","0x1","-","Meldung: Alarm Frequenzschutz"]
["f[4]","Alarm df/dt | DF/DT",41,1,"3","Bit","0x2","-","Alarm momentane oder mittlere Frequenzänderungsgeschwindigkeit."]
["f[4]","Ausl f (*)",41,1,"3","Bit","0x4","-","Meldung: Auslösung, Frequenz hat zulässigen Grenzwert verletzt"]
["f[4]","Ausl df/dt | DF/DT (*)",41,1,"3","Bit","0x8","-","Meldung: Auslösung df/dt oder DF/DT"]
["f[4]","Alarm",41,1,"3","Bit","0x10","-","Meldung: Alarm Frequenzschutz (Sammelmeldung)"]
["f[4]","Alarm delta phi",41,1,"3","Bit","0x20","-","Meldung: Alarm Vektorsprung"]
["f[4]","Ausl (*)",41,1,"3","Bit","0x40","-","Meldung: Auslösung Frequenzschutz (Sammelmeldung)"]
["f[4]","Ausl delta phi (*)",41,1,"3","Bit","0x80","-","Meldung: Auslösung delta phi"]
["f[4]","AuslBef (*)",41,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["f[5]","ExBlo1-E",42,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["f[5]","ExBlo2-E",42,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["f[5]","ExBlo AuslBef-E",42,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["f[5]","Aktiv",42,1,"3","Bit","0x8","-","Meldung: aktiv"]
["f[5]","ExBlo",42,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["f[5]","Blo durch U<",42,1,"3","Bit","0x20","-","Meldung: Modul wird durch Unterspannung blockiert."]
["f[5]","Blo AuslBef",42,1,"3","Bit","0x40","-","Meldung: Auslösebefehl blockiert"]
["f[5]","ExBlo AuslBef",42,1,"3","Bit","0x80","-","Meldung: Externe Blockade des Auslösekommandos"]
["f[5]","Alarm f",43,1,"3","Bit","0x1","-","Meldung: Alarm Frequenzschutz"]
["f[5]","Alarm df/dt | DF/DT",43,1,"3","Bit","0x2","-","Alarm momentane oder mittlere Frequenzänderungsgeschwindigkeit."]
["f[5]","Ausl f (*)",43,1,"3","Bit","0x4","-","Meldung: Auslösung, Frequenz hat zulässigen Grenzwert verletzt"]
["f[5]","Ausl df/dt | DF/DT (*)",43,1,"3","Bit","0x8","-","Meldung: Auslösung df/dt oder DF/DT"]
["f[5]","Alarm",43,1,"3","Bit","0x10","-","Meldung: Alarm Frequenzschutz (Sammelmeldung)"]
["f[5]","Alarm delta phi",43,1,"3","Bit","0x20","-","Meldung: Alarm Vektorsprung"]
["f[5]","Ausl (*)",43,1,"3","Bit","0x40","-","Meldung: Auslösung Frequenzschutz (Sammelmeldung)"]
["f[5]","Ausl delta phi (*)",43,1,"3","Bit","0x80","-","Meldung: Auslösung delta phi"]
["f[5]","AuslBef (*)",43,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]
["f[6]","ExBlo1-E",44,1,"3","Bit","0x1","-","Zustand des Moduleingangs: Externe Blockade1"]
["f[6]","ExBlo2-E",44,1,"3","Bit","0x2","-","Zustand des Moduleingangs: Externe Blockade2"]
["f[6]","ExBlo AuslBef-E",44,1,"3","Bit","0x4","-","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["f[6]","Aktiv",44,1,"3","Bit","0x8","-","Meldung: aktiv"]
["f[6]","ExBlo",44,1,"3","Bit","0x10","-","Meldung: Externe Blockade"]
["f[6]","Blo durch U<",44,1,"3","Bit","0x20","-","Meldung: Modul wird durch Unterspannung blockiert."]
["f[6]","Blo AuslBef",44,1,"3","Bit","0x40","-","Meldung: Auslösebefehl blockiert"]
["f[6]","ExBlo AuslBef",44,1,"3","Bit","0x80","-","Meldung: Externe Blockade des Auslösekommandos"]
["f[6]","Alarm f",45,1,"3","Bit","0x1","-","Meldung: Alarm Frequenzschutz"]
["f[6]","Alarm df/dt | DF/DT",45,1,"3","Bit","0x2","-","Alarm momentane oder mittlere Frequenzänderungsgeschwindigkeit."]
["f[6]","Ausl f (*)",45,1,"3","Bit","0x4","-","Meldung: Auslösung, Frequenz hat zulässigen Grenzwert verletzt"]
["f[6]","Ausl df/dt | DF/DT (*)",45,1,"3","Bit","0x8","-","Meldung: Auslösung df/dt oder DF/DT"]
["f[6]","Alarm",45,1,"3","Bit","0x10","-","Meldung: Alarm Frequenzschutz (Sammelmeldung)"]
["f[6]","Alarm delta phi",45,1,"3","Bit","0x20","-","Meldung: Alarm Vektorsprung"]
["f[6]","Ausl (*)",45,1,"3","Bit","0x40","-","Meldung: Auslösung Frequenzschutz (Sammelmeldung)"]
["f[6]","Ausl delta phi (*)",45,1,"3","Bit","0x80","-","Meldung: Auslösung delta phi"]
["f[6]","AuslBef (*)",45,1,"3","Bit","0x100","-","Meldung: Auslösebefehl"]

{"sheet":"Adjust","index":2,"n_rows":13,"n_cols":9,"rows_kept":13,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["Datum/Uhrzeit","y",32500,6,"3 16","Short","Word 0","-","Jahr"]
["Datum/Uhrzeit","m",32500,6,"3 16","Short","Word 1","-","Monat"]
["Datum/Uhrzeit","d",32500,6,"3 16","Short","Word 2","-","Tage"]
["Datum/Uhrzeit","h",32500,6,"3 16","Short","Word 3","-","Stunden"]
["Datum/Uhrzeit","min",32500,6,"3 16","Short","Word 4","-","Minute"]
["Datum/Uhrzeit","ms",32500,6,"3 16","Short","Word 5","-","Millisekunde"]
["Fehlerrek","Aufz. Nr.",50000,9,"3 16","Short","Word 0","-","Aufzeichungsnummer"]
["Fehlerrek","Ausl.-Ursache",50000,9,"3 16","Short","Word 1","-","Codierung der Auslöseursache. Bei mehreren gleichzeitigen Auslöseursachen wird die primäre Ursache ausgewählt. Im Falle einer weiteren, späteren Auslösung überschreibt die neue Ursache die vorherige. Die Codierungen der Auslöseursachen sind in der SCADA-Dokumentation aufgeführt."]
["Fehlerrek","Alarm Ursache",50000,9,"3 16","Short","Word 2","-","Letze Alarmusache diese entspricht der letzten Alarmursache im Fehlerrekorder. Siehe auch Scada-Dokumentation um die Zuordnung Code->Ursache einsehen zu können."]
["Fehlerrek","Störfall-Nr.",50000,9,"3 16","Short","Word 3","-","Störfallnummer"]
["Fehlerrek","Netzstör-Nr.",50000,9,"3 16","Short","Word 4","-","Netzstörungsnummer: Hier wird jeder Fehler, d.h. jede Generalanregung (Signal »Schutz . Alarm«) gezählt, jedoch nur dann, wenn nicht zugleich schon eine Wiedereinschaltung (Signal »AWE . läuft«) aktiv ist. (Anmerkung: Im Gegensatz hierzu zählt die »Störfall-Nr.« jeden Netzfehler, unabhängig von der Wiedereinschaltung. Für Schutzgeräte ohne AWE-Modul sind diese beiden Zähler prinzipiell gleichbedeutend.)"]
["Fehlerrek","Zeitstempel:",50000,9,"3 16","long long","Word 5- Word 8","-","Zeitstempel in Millisekunden seit 1970"]

{"sheet":"Command","index":3,"n_rows":36,"n_cols":9,"rows_kept":36,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["Quittierung","LEDs",22000,1,"5","0xFF00","Word 0","-","LEDs"]
["Quittierung","Ausgangsrelais",22001,1,"5","0xFF00","Word 0","-","Ausgangsrelais"]
["Quittierung","Leittechnik",22002,1,"5","0xFF00","Word 0","-","Scada"]
["Quittierung","Gerät",22003,1,"5","0xFF00","Word 0","-","Gerät"]
["Quittierung","Quit AuslBef",22005,1,"5","0xFF00","Word 0","-","Meldung: Quittierung des Auslösebefehls"]
["Reset","Modbus Diagnose-Zähler",22006,1,"5","0xFF00","Word 0","-","Modbus Diagnose-Zähler"]
["Reset","Res alle EnergieZ",22011,1,"5","0xFF00","Word 0","-","Reset aller Energiezähler"]
["Leittechnik-Bef","Rang Leitt-Bef 1",22020,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 2",22021,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 3",22022,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 4",22023,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 5",22024,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 6",22025,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 7",22026,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 8",22027,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 9",22028,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 10",22029,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 11",22030,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 12",22031,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 13",22032,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 14",22033,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 15",22034,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Leittechnik-Bef","Rang Leitt-Bef 16",22035,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Rangierbarer Leittechnik-Befehl"]
["Fehlerrek","Res alle Aufzng",22040,1,"5","0xFF00","Word 0","-","Alle Aufzeichnungen löschen"]
["Satz-Umschaltung","Scada PS1",22050,1,"5","0xFF00","Word 0","-","Scada Parametersatz1"]
["Satz-Umschaltung","Scada PS2",22051,1,"5","0xFF00","Word 0","-","Scada Parametersatz2"]
["Satz-Umschaltung","Scada PS3",22052,1,"5","0xFF00","Word 0","-","Scada Parametersatz3"]
["Satz-Umschaltung","Scada PS4",22053,1,"5","0xFF00","Word 0","-","Scada Parametersatz4"]
["LichtbRed Modus","LichtbRed SCADA",22054,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Meldung: Lichtbogenreduktion SCADA Modus"]
["SG","SG SteuerBef1",22100,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Steuerbefehl Schaltgerät"]
["SG","SG SteuerBef2",22101,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Steuerbefehl Schaltgerät"]
["SG","SG SteuerBef3",22102,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Steuerbefehl Schaltgerät"]
["SG","SG SteuerBef4",22103,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Steuerbefehl Schaltgerät"]
["SG","SG SteuerBef5",22104,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Steuerbefehl Schaltgerät"]
["SG","SG SteuerBef6",22105,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Steuerbefehl Schaltgerät"]

{"sheet":"Measure","index":4,"n_rows":321,"n_cols":9,"rows_kept":321,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["AWE","Gesamt Z",20164,2,"4","Float IEE754","Word 0","-","Gesamtanzahl aller durchgeführten Automatischen Wiedereinschaltversuche"]
["AWE","Z fehlgeschl",20166,2,"4","Float IEE754","Word 0","-","Gesamtanzahl erfolgloser Automatischer Wiedereinschaltversuche"]
["AWE","Z erfolgr",20168,2,"4","Float IEE754","Word 0","-","Gesamtanzahl erfolgreicher Automatischer Wiedereinschaltungen"]
["AWE","Z Service Alarm1",20170,2,"4","Float IEE754","Word 0","-","Noch verbleibende Anzahl AWEs bis zum Service-Alarm 1"]
["AWE","Z Service Alarm2",20172,2,"4","Float IEE754","Word 0","-","Noch verbleibende Anzahl AWEs bis zum Service-Alarm 2"]
["AWE","AWE Versuch Nr.",20188,2,"4","Float IEE754","Word 0","-","Zähler - Automatische Wiedereinschaltversuche"]
["AWE","Max Schüsse / h Z",20374,2,"4","Float IEE754","Word 0","-","Zähler für die höchstzulässige Anzahl von Wiedereinschaltversuchen pro Stunde."]
["AnEing[1]","Wert",20896,2,"4","Float IEE754","Word 0","%","Gemessener Eingangswert in Prozent."]
["AnEing[2]","Wert",20900,2,"4","Float IEE754","Word 0","%","Gemessener Eingangswert in Prozent."]
["Datum/Uhrzeit","y",20000,6,"4","Short","Word 0","-","Jahr"]
["Datum/Uhrzeit","m",20000,6,"4","Short","Word 1","-","Monat"]
["Datum/Uhrzeit","d",20000,6,"4","Short","Word 2","-","Tage"]
["Datum/Uhrzeit","h",20000,6,"4","Short","Word 3","-","Stunden"]
["Datum/Uhrzeit","min",20000,6,"4","Short","Word 4","-","Minute"]
["Datum/Uhrzeit","ms",20000,6,"4","Short","Word 5","-","Millisekunde"]
["IRIG-B","Anz der Pegeländer",20298,2,"4","Float IEE754","Word 0","-","Anzahl der Pegeländerungen. Mit diesem Zähler kann überprüft werden, ob ein Signal am IRIG-G Eingang anliegt."]
["IRIG-B","AnzDatüblöckeFeh",20300,2,"4","Float IEE754","Word 0","-","Anzahl fehlerhafter Datenübertragungsblöcke.  Physikalisch zerstörter Datenübertragungsblock."]
["IRIG-B","AnzDatüblöckeOK",20302,2,"4","Float IEE754","Word 0","-","Anzahl korrekt übertragener Datenübertragungsblöcke."]
["LVRT[1]","Z Anz SpgEinbr ges",24092,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl an Spannungseinbrüchen"]
["LVRT[1]","Z Anz SpgsEinbr in t-LVRT",24094,2,"4","Float IEE754","Word 0","-","Anzahl von Spannungseinbrüchen während t-LVRT."]
["LVRT[1]","Z Anz SpgsEinbr Ausl",24096,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl an Spannungseinbrüchen, die zu einer Auslösung geführt haben."]
["LVRT[2]","Z Anz SpgEinbr ges",24138,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl an Spannungseinbrüchen"]
["LVRT[2]","Z Anz SpgsEinbr in t-LVRT",24140,2,"4","Float IEE754","Word 0","-","Anzahl von Spannungseinbrüchen während t-LVRT."]
["LVRT[2]","Z Anz SpgsEinbr Ausl",24142,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl an Spannungseinbrüchen, die zu einer Auslösung geführt haben."]
["Modbus","Konf Messw1",23000,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw2",23002,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw3",23004,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw4",23006,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw5",23008,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw6",23010,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw7",23012,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw8",23014,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw9",23016,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw10",23018,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw11",23020,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw12",23022,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw13",23024,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw14",23026,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw15",23028,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["Modbus","Konf Messw16",23030,2,"4","Float IEE754","Word 0","-","Konfigurierbarer (gemappte) Messwerte. Diese können verwendet werden um Messwerte an den Modbus Master zu übermitteln."]
["PQSZ","cos phi ",20152,2,"4","Float IEE754","Word 0","-","Messwert (berechnet): Leistungsfaktor: Vorzeichenkonvention: sign(LF) = sign(P)"]
["PQSZ","P ",20154,2,"4","Float IEE754","Word 0","W","Messwert (berechnet): Wirkleistung (P- = abgegebene Wirkleistung, P+ = aufgenommene Wirkleistung) (Grundwelle)"]
["PQSZ","Q ",20156,2,"4","Float IEE754","Word 0","VAr ","Messwert (berechnet): Blindleistung (Q- = abgegebene Blindleistung, Q+ = aufgenommene Blindleistung) (Grundwelle)"]
["PQSZ","S ",20158,2,"4","Float IEE754","Word 0","VA","Messwert (berechnet): Scheinleistung (Grundwelle)"]
["PQSZ","Wp+",20174,2,"4","Float IEE754","Word 0","kWh","Aufgenommene Wirkarbeit"]
["PQSZ","Wp-",20176,2,"4","Float IEE754","Word 0","kWh","Abgegebene Wirkarbeit"]
["PQSZ","Wq+",20178,2,"4","Float IEE754","Word 0","kVArh","Aufgenommene Blindarbeit"]
["PQSZ","Wq-",20180,2,"4","Float IEE754","Word 0","kVArh","Abgegebene Blindarbeit"]
["PQSZ","P RMS",20452,2,"4","Float IEE754","Word 0","W","Messwert (berechnet): Wirkleistung (P- = abgegebene Wirkleistung, P+ = aufgenommene Wirkleistung) (RMS)"]
["PQSZ","S RMS",20454,2,"4","Float IEE754","Word 0","VA","Messwert (berechnet): Scheinleistung (RMS)"]
["PQSZ","cos phi RMS",20456,2,"4","Float IEE754","Word 0","-","Messwert (berechnet): Leistungsfaktor: Vorzeichenkonvention: sign(LF) = sign(P)"]
["PQSZ","Wp Net",20460,2,"4","Float IEE754","Word 0","kWh","Netto Betrag Wirkleistungsstunden"]
["PQSZ","Wq Net",20462,2,"4","Float IEE754","Word 0","kVArh","Netto Betrag Blindleistungsstunden"]
["PQSZ","Ws Net",20464,2,"4","Float IEE754","Word 0","kVAh","Netto Betrag Scheinleistungsstunden"]
["PQSZ","P1",20496,2,"4","Float IEE754","Word 0","W","Messwert (berechnet): Wirkleistung im Mitsystem (P- = abgegebene Wirkleistung, P+ = aufgenommene Wirkleistung)"]
["PQSZ","Q1",20498,2,"4","Float IEE754","Word 0","VAr ","Messwert (berechnet): Blindleistung im Mitsystem (Q- = abgegebene Blindleistung, Q+ = aufgenommene Blindleistung)"]
["PQSZ","cos phi max",21092,2,"4","Float IEE754","Word 0","-","Maximalwert des Leistungsfaktors: Vorzeichenkonvention: sign(LF) = sign(P)"]
["PQSZ","cos phi min",21094,2,"4","Float IEE754","Word 0","-","Minimalwert des Leistungsfaktors: Vorzeichenkonvention: sign(LF) = sign(P)"]
["PQSZ","P mit (Bezug)",21556,2,"4","Float IEE754","Word 0","W","Mittelwert der Wirkleistung"]
["PQSZ","P max",21558,2,"4","Float IEE754","Word 0","W","Maximalwert der Wirkleistung"]
["PQSZ","P min",21560,2,"4","Float IEE754","Word 0","W","Minimalwert der Wirkleistung"]
["PQSZ","S mit (Bezug)",21562,2,"4","Float IEE754","Word 0","VA","Mittelwert der Scheinleistung"]
["PQSZ","S max",21564,2,"4","Float IEE754","Word 0","VA","Maximalwert der Scheinleistung"]
["PQSZ","S min",21566,2,"4","Float IEE754","Word 0","VA","Minimalwert der Scheinleistung"]
["PQSZ","cos phi max RMS",21570,2,"4","Float IEE754","Word 0","-","Maximalwert des Leistungsfaktors: Vorzeichenkonvention: sign(LF) = sign(P)"]
["PQSZ","cos phi min RMS",21572,2,"4","Float IEE754","Word 0","-","Minimalwert des Leistungsfaktors: Vorzeichenkonvention: sign(LF) = sign(P)"]
["PQSZ","Q mit (Bezug)",21574,2,"4","Float IEE754","Word 0","VAr ","Mittelwert der Blindleistung"]
["PQSZ","Q max",21576,2,"4","Float IEE754","Word 0","VAr ","Maximalwert der Blindleistung"]
["PQSZ","Q min",21578,2,"4","Float IEE754","Word 0","VAr ","Minimalwert der Blindleistung"]
["PQSZ","P Max (Bezug)",21790,2,"4","Float IEE754","Word 0","W","Schleppzeiger der Wirkleistung (Maximalwert)"]
["PQSZ","Q Max (Bezug)",21792,2,"4","Float IEE754","Word 0","VAr ","Schleppzeiger der Blindleistung (Maximalwert)"]
["PQSZ","S Max (Bezug)",21794,2,"4","Float IEE754","Word 0","VA","Schleppzeiger der Scheinleistung (Maximalwert)"]
["PQSZ - Fehlerwert","cos phi ",50152,2,"4","Float IEE754","Word 0","-","Messwert (berechnet): Leistungsfaktor: Vorzeichenkonvention: sign(LF) = sign(P) , wie im Fehlerrekorder gespeichert"]
["PQSZ - Fehlerwert","P ",50154,2,"4","Float IEE754","Word 0","W","Messwert (berechnet): Wirkleistung (P- = abgegebene Wirkleistung, P+ = aufgenommene Wirkleistung) (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["PQSZ - Fehlerwert","Q ",50156,2,"4","Float IEE754","Word 0","VAr ","Messwert (berechnet): Blindleistung (Q- = abgegebene Blindleistung, Q+ = aufgenommene Blindleistung) (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["PQSZ - Fehlerwert","S ",50158,2,"4","Float IEE754","Word 0","VA","Messwert (berechnet): Scheinleistung (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["PQSZ - Fehlerwert","P RMS",50452,2,"4","Float IEE754","Word 0","W","Messwert (berechnet): Wirkleistung (P- = abgegebene Wirkleistung, P+ = aufgenommene Wirkleistung) (RMS) , wie im Fehlerrekorder gespeichert"]
["PQSZ - Fehlerwert","S RMS",50454,2,"4","Float IEE754","Word 0","VA","Messwert (berechnet): Scheinleistung (RMS) , wie im Fehlerrekorder gespeichert"]
["PQSZ - Fehlerwert","cos phi RMS",50456,2,"4","Float IEE754","Word 0","-","Messwert (berechnet): Leistungsfaktor: Vorzeichenkonvention: sign(LF) = sign(P) , wie im Fehlerrekorder gespeichert"]
["PQSZ - Fehlerwert","P1",50496,2,"4","Float IEE754","Word 0","W","Messwert (berechnet): Wirkleistung im Mitsystem (P- = abgegebene Wirkleistung, P+ = aufgenommene Wirkleistung) , wie im Fehlerrekorder gespeichert"]
["PQSZ - Fehlerwert","Q1",50498,2,"4","Float IEE754","Word 0","VAr ","Messwert (berechnet): Blindleistung im Mitsystem (Q- = abgegebene Blindleistung, Q+ = aufgenommene Blindleistung) , wie im Fehlerrekorder gespeichert"]
["SG[1]","Sum Abschalt IL1",20800,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[1]","Sum Abschalt IL2",20802,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[1]","Sum Abschalt IL3",20804,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[1]","Sum Ik/h",20806,2,"4","Float IEE754","Word 0","kA","Kumulierte Summe der Abschaltströme pro Stunde."]
["SG[1]","LS-Verschleiß",20808,2,"4","Float IEE754","Word 0","%","Verschleißgrad des Leistungsschalters. (100% bedeutet, dass der Schalter gewartet werden muss.)"]
["SG[1]","AuslBef Z",20810,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl Auslösungen des Schaltgeräts."]
["SG[2]","Sum Abschalt IL1",20812,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[2]","Sum Abschalt IL2",20814,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[2]","Sum Abschalt IL3",20816,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[2]","Sum Ik/h",20818,2,"4","Float IEE754","Word 0","kA","Kumulierte Summe der Abschaltströme pro Stunde."]
["SG[2]","LS-Verschleiß",20820,2,"4","Float IEE754","Word 0","%","Verschleißgrad des Leistungsschalters. (100% bedeutet, dass der Schalter gewartet werden muss.)"]
["SG[2]","AuslBef Z",20822,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl Auslösungen des Schaltgeräts."]
["SG[3]","Sum Abschalt IL1",20824,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[3]","Sum Abschalt IL2",20826,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[3]","Sum Abschalt IL3",20828,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[3]","Sum Ik/h",20830,2,"4","Float IEE754","Word 0","kA","Kumulierte Summe der Abschaltströme pro Stunde."]
["SG[3]","LS-Verschleiß",20832,2,"4","Float IEE754","Word 0","%","Verschleißgrad des Leistungsschalters. (100% bedeutet, dass der Schalter gewartet werden muss.)"]
["SG[3]","AuslBef Z",20834,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl Auslösungen des Schaltgeräts."]
["SG[4]","Sum Abschalt IL1",20836,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[4]","Sum Abschalt IL2",20838,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[4]","Sum Abschalt IL3",20840,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[4]","Sum Ik/h",20842,2,"4","Float IEE754","Word 0","kA","Kumulierte Summe der Abschaltströme pro Stunde."]
["SG[4]","LS-Verschleiß",20844,2,"4","Float IEE754","Word 0","%","Verschleißgrad des Leistungsschalters. (100% bedeutet, dass der Schalter gewartet werden muss.)"]
["SG[4]","AuslBef Z",20846,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl Auslösungen des Schaltgeräts."]
["SG[5]","Sum Abschalt IL1",20848,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[5]","Sum Abschalt IL2",20850,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[5]","Sum Abschalt IL3",20852,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[5]","Sum Ik/h",20854,2,"4","Float IEE754","Word 0","kA","Kumulierte Summe der Abschaltströme pro Stunde."]
["SG[5]","LS-Verschleiß",20856,2,"4","Float IEE754","Word 0","%","Verschleißgrad des Leistungsschalters. (100% bedeutet, dass der Schalter gewartet werden muss.)"]
["SG[5]","AuslBef Z",20858,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl Auslösungen des Schaltgeräts."]
["SG[6]","Sum Abschalt IL1",20860,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[6]","Sum Abschalt IL2",20862,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[6]","Sum Abschalt IL3",20864,2,"4","Float IEE754","Word 0","A","Summe der Abschaltströme Phase"]
["SG[6]","Sum Ik/h",20866,2,"4","Float IEE754","Word 0","kA","Kumulierte Summe der Abschaltströme pro Stunde."]
["SG[6]","LS-Verschleiß",20868,2,"4","Float IEE754","Word 0","%","Verschleißgrad des Leistungsschalters. (100% bedeutet, dass der Schalter gewartet werden muss.)"]
["SG[6]","AuslBef Z",20870,2,"4","Float IEE754","Word 0","-","Zähler Gesamtanzahl Auslösungen des Schaltgeräts."]
["SpW","f ",20128,2,"4","Float IEE754","Word 0","Hz","Messwert: Frequenz"]
["SpW","UL12 ",20130,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (Grundwelle)"]
["SpW","UL23 ",20132,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (Grundwelle)"]
["SpW","UL31 ",20134,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (Grundwelle)"]
["SpW","UL1 ",20136,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (Grundwelle)"]
["SpW","UL2 ",20138,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (Grundwelle)"]
["SpW","UL3 ",20140,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (Grundwelle)"]
["SpW","UX gem ",20142,2,"4","Float IEE754","Word 0","V","Messwert (gemessen): UX (Grundwelle)"]
["SpW","U0 ",20146,2,"4","Float IEE754","Word 0","V","Messwert (berechnet): Symmetrische Komponenten Spannung Nullsystem(Grundwelle)"]
["SpW","U1 ",20148,2,"4","Float IEE754","Word 0","V","Messwert (berechnet): Symmetrische Komponenten Spannung Mitsystem(Grundwelle)"]
["SpW","U2 ",20150,2,"4","Float IEE754","Word 0","V","Messwert (berechnet): Symmetrische Komponenten Spannung Gegensystem(Grundwelle)"]
["SpW","UE err ",20162,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UE (Grundwelle)"]
["SpW","phi UE err",20386,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UE err\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi UX gem",20388,2,"4","Float IEE754","Word 0","°","Messwert: Phasenlage Spannungszeiger UX gem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi UL12",20390,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL12\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi UL1",20392,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL1\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi UL23",20394,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL23\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi UL2",20396,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL2\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi UL31",20398,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL31\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi UL3",20400,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL3\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi U0",20402,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Nullsystem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi U1",20404,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Mitsystem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","phi U2",20406,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Gegensystem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["SpW","UL1  THD",20408,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UL1 Total Harmonic Distortion"]
["SpW","UL12 THD",20410,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): U12 Total Harmonic Distortion"]
["SpW","UL2 THD",20412,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UL2 Total Harmonic Distortion"]
["SpW","UL23 THD",20414,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): U23 Total Harmonic Distortion"]
["SpW","UL3 THD",20416,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UL3 Total Harmonic Distortion"]
["SpW","UL31 THD",20418,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): U31 Total Harmonic Distortion"]
["SpW","%UL1  THD",20420,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): UL1 Total Harmonic Distortion bezogen auf die Grundwelle"]
["SpW","%UL12 THD",20422,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): U12 Total Harmonic Distortion bezogen auf die Grundwelle"]
["SpW","%UL2 THD",20424,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): UL2 Total Harmonic Distortion bezogen auf die Grundwelle"]
["SpW","%UL23 THD",20426,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): U23 Total Harmonic Distortion bezogen auf die Grundwelle"]
["SpW","%UL3 THD",20428,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): UL3 Total Harmonic Distortion bezogen auf die Grundwelle"]
["SpW","%UL31 THD",20430,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): U31 Total Harmonic Distortion bezogen auf die Grundwelle"]
["SpW","UE err RMS",20432,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UE (RMS)"]
["SpW","UX gem RMS",20434,2,"4","Float IEE754","Word 0","V","Messwert (gemessen): UX (RMS)"]
["SpW","UL1 RMS",20436,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (RMS)"]
["SpW","UL12 RMS",20438,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (RMS)"]
["SpW","UL2 RMS",20440,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (RMS)"]
["SpW","UL23 RMS",20442,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (RMS)"]
["SpW","UL3 RMS",20444,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (RMS)"]
["SpW","UL31 RMS",20446,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (RMS)"]
["SpW","%(U2/U1)",20450,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): U2/U1, Drehfeldrichtung wird automatisch berücksichtigt."]
["SpW","f max",21002,2,"4","Float IEE754","Word 0","Hz","Frequenzmaximalwert"]
["SpW","f min",21004,2,"4","Float IEE754","Word 0","Hz","Frequenzminimalwert"]
["SpW","U1 max ",21044,2,"4","Float IEE754","Word 0","V","Maximalwert: Symmetrische Komponenten Spannung Mitsystem(Grundwelle)"]
["SpW","U1 min ",21046,2,"4","Float IEE754","Word 0","V","Minimalwert: Symmetrische Komponenten Spannung Mitsystem(Grundwelle)"]
["SpW","U2 max ",21050,2,"4","Float IEE754","Word 0","V","Maximalwert: Symmetrische Komponenten Spannung Gegensystem(Grundwelle)"]
["SpW","U2 min ",21052,2,"4","Float IEE754","Word 0","V","Minimalwert: Symmetrische Komponenten Spannung Gegensystem(Grundwelle)"]
["SpW","delta phi",21126,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Vektorsprung"]
["SpW","df/dt",21128,2,"4","Float IEE754","Word 0","Hz/s","Messwert (errechnet): Frequenzänderungsgeschwindigkeit"]
["SpW","UE err max RMS",21498,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UX Maximalwert (RMS)"]
["SpW","UE err min RMS",21500,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UX Minimalwert (RMS)"]
["SpW","UX gem max RMS",21504,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UX Maximalwert (RMS)"]
["SpW","UX gem min RMS",21506,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UX Minimalwert (RMS)"]
["SpW","UL12 mit RMS",21508,2,"4","Float IEE754","Word 0","V","UL12 Mittelwert (RMS)"]
["SpW","UL12 max RMS",21510,2,"4","Float IEE754","Word 0","V","UL12 Maximalwert (RMS)"]
["SpW","UL12 min RMS",21512,2,"4","Float IEE754","Word 0","V","UL12 Minimalwert (RMS)"]
["SpW","UL1 mit RMS",21514,2,"4","Float IEE754","Word 0","V","UL1 Mittelwert (RMS)"]
["SpW","UL1 max RMS",21516,2,"4","Float IEE754","Word 0","V","UL1 Maximalwert (RMS)"]
["SpW","UL1 min RMS",21518,2,"4","Float IEE754","Word 0","V","UL1 Minimalwert (RMS)"]
["SpW","UL23 mit RMS",21520,2,"4","Float IEE754","Word 0","V","UL23 Mittelwert (RMS)"]
["SpW","UL23 max RMS",21522,2,"4","Float IEE754","Word 0","V","UL23 Maximalwert (RMS)"]
["SpW","UL23 min RMS",21524,2,"4","Float IEE754","Word 0","V","UL23 Minimalwert (RMS)"]
["SpW","UL2 mit RMS",21526,2,"4","Float IEE754","Word 0","V","UL2 Mittelwert (RMS)"]
["SpW","UL2 max RMS",21528,2,"4","Float IEE754","Word 0","V","UL2 Maximalwert (RMS)"]
["SpW","UL2 min RMS",21530,2,"4","Float IEE754","Word 0","V","UL2 Minimalwert (RMS)"]
["SpW","UL31 mit RMS",21532,2,"4","Float IEE754","Word 0","V","UL31 Mittelwert (RMS)"]
["SpW","UL31 max RMS",21534,2,"4","Float IEE754","Word 0","V","UL31 Maximalwert (RMS)"]
["SpW","UL31 min RMS",21536,2,"4","Float IEE754","Word 0","V","UL31 Minimalwert (RMS)"]
["SpW","UL3 mit RMS",21538,2,"4","Float IEE754","Word 0","V","UL3 Mittelwert (RMS)"]
["SpW","UL3 max RMS",21540,2,"4","Float IEE754","Word 0","V","UL3 Maximalwert (RMS)"]
["SpW","UL3 min RMS",21542,2,"4","Float IEE754","Word 0","V","UL3 Minimalwert (RMS)"]
["SpW","%(U2/U1) max",21552,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): U2/U1  Maximalwert, Drehfeldrichtung wird automatisch berücksichtigt "]
["SpW","%(U2/U1) min",21554,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): U2/U1 Minimalwert, Drehfeldrichtung wird automatisch berücksichtigt "]
["SpW - Fehlerwert","f ",50128,2,"4","Float IEE754","Word 0","Hz","Messwert: Frequenz , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL12 ",50130,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL23 ",50132,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL31 ",50134,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL1 ",50136,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL2 ",50138,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL3 ",50140,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UX gem ",50142,2,"4","Float IEE754","Word 0","V","Messwert (gemessen): UX (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","U0 ",50146,2,"4","Float IEE754","Word 0","V","Messwert (berechnet): Symmetrische Komponenten Spannung Nullsystem(Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","U1 ",50148,2,"4","Float IEE754","Word 0","V","Messwert (berechnet): Symmetrische Komponenten Spannung Mitsystem(Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","U2 ",50150,2,"4","Float IEE754","Word 0","V","Messwert (berechnet): Symmetrische Komponenten Spannung Gegensystem(Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UE err ",50162,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UE (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","phi UE err",50386,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UE err\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","phi UX gem",50388,2,"4","Float IEE754","Word 0","°","Messwert: Phasenlage Spannungszeiger UX gem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","phi UL12",50390,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL12\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","phi UL1",50392,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL1\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","phi UL23",50394,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL23\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","phi UL2",50396,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL2\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","phi UL31",50398,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL31\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","phi UL3",50400,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Spannungszeiger UL3\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UE err RMS",50432,2,"4","Float IEE754","Word 0","V","Messwert (errechnet): UE (RMS) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UX gem RMS",50434,2,"4","Float IEE754","Word 0","V","Messwert (gemessen): UX (RMS) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL1 RMS",50436,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (RMS) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL12 RMS",50438,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (RMS) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL2 RMS",50440,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (RMS) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL23 RMS",50442,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (RMS) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL3 RMS",50444,2,"4","Float IEE754","Word 0","V","Messwert: Leiter-Erd-Spannung (RMS) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","UL31 RMS",50446,2,"4","Float IEE754","Word 0","V","Messwert: Außenleiterspannung (RMS) , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","delta phi",51126,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Vektorsprung , wie im Fehlerrekorder gespeichert"]
["SpW - Fehlerwert","df/dt",51128,2,"4","Float IEE754","Word 0","Hz/s","Messwert (errechnet): Frequenzänderungsgeschwindigkeit , wie im Fehlerrekorder gespeichert"]
["StW","IL1 ",20100,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (Grundwelle)"]
["StW","IL2 ",20102,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (Grundwelle)"]
["StW","IL3 ",20104,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (Grundwelle)"]
["StW","IE gem ",20106,2,"4","Float IEE754","Word 0","A","Messwert (gemessen): IE (Grundwelle)"]
["StW","I0 ",20114,2,"4","Float IEE754","Word 0","A","Messwert (berechnet): Nullstrom (Grundwelle)"]
["StW","I1 ",20116,2,"4","Float IEE754","Word 0","A","Messwert (berechnet): Strom Mitsystem (Grundwelle)"]
["StW","I2 ",20118,2,"4","Float IEE754","Word 0","A","Messwert (berechnet): Strom Gegensystem (Grundwelle)"]
["StW","IL1 H2 ",20120,2,"4","Float IEE754","Word 0","%","Messwert: 2. Harmonische/Grundwelle von IL1"]
["StW","IL2 H2 ",20122,2,"4","Float IEE754","Word 0","%","Messwert: 2. Harmonische/Grundwelle von IL2"]
["StW","IL3 H2 ",20124,2,"4","Float IEE754","Word 0","%","Messwert: 2. Harmonische/Grundwelle von IL3"]
["StW","IE err ",20160,2,"4","Float IEE754","Word 0","A","Messwert (errechnet): IE (Grundwelle)"]
["StW","phi IE err",20200,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IE err\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["StW","phi IE gem",20202,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IE gem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["StW","phi IL1",20204,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IL1\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["StW","phi IL2",20206,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IL2\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["StW","phi IL3",20208,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IL3\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["StW","IL1 THD",20210,2,"4","Float IEE754","Word 0","A","Messwert (errechnet): IL1 Verzerrungsstrom / gesamter Oberschwingungsstrom "]
["StW","IL2 THD",20212,2,"4","Float IEE754","Word 0","A","Messwert (errechnet): IL2 Verzerrungsstrom / gesamter Oberschwingungsstrom "]
["StW","IL3 THD",20214,2,"4","Float IEE754","Word 0","A","Messwert (errechnet): IL3 Verzerrungsstrom / gesamter Oberschwingungsstrom "]
["StW","%IL1 THD",20216,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): IL1 Total Harmonic Distortion"]
["StW","%IL2 THD",20218,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): IL2 Total Harmonic Distortion"]
["StW","%IL3 THD",20220,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): IL3 Total Harmonic Distortion"]
["StW","IL1 RMS",20316,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (RMS)"]
["StW","IL2 RMS",20318,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (RMS)"]
["StW","IL3 RMS",20320,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (RMS)"]
["StW","IE gem RMS",20322,2,"4","Float IEE754","Word 0","A","Messwert (gemessen): IE (RMS)"]
["StW","IE err RMS",20324,2,"4","Float IEE754","Word 0","A","Messwert (errechnet): IE (RMS)"]
["StW","%(I2/I1)",20376,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): I2/I1, Drehfeldrichtung wird automatisch berücksichtigt."]
["StW","phi I0",20378,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Nullsystem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["StW","phi I1",20380,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Mitsystem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["StW","phi I2",20382,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Gegensystem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude."]
["StW","I1 max ",21074,2,"4","Float IEE754","Word 0","A","Maximalwert Strom Mitsystem (Grundwelle)"]
["StW","I1 min ",21076,2,"4","Float IEE754","Word 0","A","Minimalwert Strom Mitsystem (Grundwelle)"]
["StW","I2 max ",21080,2,"4","Float IEE754","Word 0","A","Maximalwert Strom Gegensystem (Grundwelle)"]
["StW","I2 min ",21082,2,"4","Float IEE754","Word 0","A","Minimalwert Strom Gegensystem (Grundwelle)"]
["StW","IL1 mit RMS",21130,2,"4","Float IEE754","Word 0","A","IL1 Mittelwert (RMS)"]
["StW","IL2 mit RMS",21132,2,"4","Float IEE754","Word 0","A","IL2 Mittelwert (RMS)"]
["StW","IL3 mit RMS",21134,2,"4","Float IEE754","Word 0","A","IL3 Mittelwert (RMS)"]
["StW","IL1 max RMS",21136,2,"4","Float IEE754","Word 0","A","IL1 Maximalwert (RMS)"]
["StW","IL2 max RMS",21138,2,"4","Float IEE754","Word 0","A","IL2 Maximalwert (RMS)"]
["StW","IL3 max RMS",21140,2,"4","Float IEE754","Word 0","A","IL3 Maximalwert (RMS)"]
["StW","IL1 min RMS",21142,2,"4","Float IEE754","Word 0","A","IL1 Minimalwert (RMS)"]
["StW","IL2 min RMS",21144,2,"4","Float IEE754","Word 0","A","IL2 Minimalwert (RMS)"]
["StW","IL3 min RMS",21146,2,"4","Float IEE754","Word 0","A","IL3 Minimalwert (RMS)"]
["StW","IL1 H2 max",21228,2,"4","Float IEE754","Word 0","%","2. Harmonische/Grundwelle von IL1 Maximalwert"]
["StW","IL1 H2 min",21230,2,"4","Float IEE754","Word 0","%","2. Harmonische/Grundwelle von IL1 Minimalwert"]
["StW","IL2 H2 max",21234,2,"4","Float IEE754","Word 0","%","2. Harmonische/Grundwelle von IL2 Maximalwert"]
["StW","IL2 H2 min",21236,2,"4","Float IEE754","Word 0","%","2. Harmonische/Grundwelle von IL2 Minimalwert"]
["StW","IL3 H2 max",21240,2,"4","Float IEE754","Word 0","%","2. Harmonische/Grundwelle von IL3 Maximalwert"]
["StW","IL3 H2 min",21242,2,"4","Float IEE754","Word 0","%","2. Harmonische/Grundwelle von IL3 Minimalwert"]
["StW","IE err max RMS",21456,2,"4","Float IEE754","Word 0","A","Messwert (errechnet): IE Maximalwert (RMS)"]
["StW","IE err min RMS",21458,2,"4","Float IEE754","Word 0","A","Messwert (errechnet): IE Minimalwert (RMS)"]
["StW","IE gem max RMS",21462,2,"4","Float IEE754","Word 0","A","Messwert: IE Maximalwert (RMS)"]
["StW","IE gem min RMS",21464,2,"4","Float IEE754","Word 0","A","Messwert: IE Minimalwert (RMS)"]
["StW","%(I2/I1)  max",21468,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): I2/I1 Maximalwert, Drehfeldrichtung wird automatisch berücksichtigt "]
["StW","%(I2/I1)  min",21470,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): I2/I1 Minimalwert, Drehfeldrichtung wird automatisch berücksichtigt "]
["StW","IL1 Max (Bezug)",21784,2,"4","Float IEE754","Word 0","A","Schleppzeiger des Stroms in L1 (Maximalwert)."]
["StW","IL2 Max (Bezug)",21786,2,"4","Float IEE754","Word 0","A","Schleppzeiger des Stroms in L2 (Maximalwert)."]
["StW","IL3 Max (Bezug)",21788,2,"4","Float IEE754","Word 0","A","Schleppzeiger des Stroms in L3 (Maximalwert)."]
["StW - Fehlerwert","IL1 ",50100,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IL2 ",50102,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IL3 ",50104,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IE gem ",50106,2,"4","Float IEE754","Word 0","A","Messwert (gemessen): IE (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","I0 ",50114,2,"4","Float IEE754","Word 0","A","Messwert (berechnet): Nullstrom (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","I1 ",50116,2,"4","Float IEE754","Word 0","A","Messwert (berechnet): Strom Mitsystem (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","I2 ",50118,2,"4","Float IEE754","Word 0","A","Messwert (berechnet): Strom Gegensystem (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IL1 H2 ",50120,2,"4","Float IEE754","Word 0","%","Messwert: 2. Harmonische/Grundwelle von IL1 , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IL2 H2 ",50122,2,"4","Float IEE754","Word 0","%","Messwert: 2. Harmonische/Grundwelle von IL2 , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IL3 H2 ",50124,2,"4","Float IEE754","Word 0","%","Messwert: 2. Harmonische/Grundwelle von IL3 , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IE err ",50160,2,"4","Float IEE754","Word 0","A","Messwert (errechnet): IE (Grundwelle) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","phi IE err",50200,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IE err\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","phi IE gem",50202,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IE gem\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","phi IL1",50204,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IL1\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","phi IL2",50206,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IL2\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","phi IL3",50208,2,"4","Float IEE754","Word 0","°","Messwert (errechnet): Phasenlage Stromzeiger IL3\\nReferenzphase ist erforderlich zur Berechnung der Phasenlage. Hierfür wählt das Schutzgerät den ersten Spannungs- (oder Strom-) Messkanal mit genügend großer Amplitude. , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IL1 RMS",50316,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (RMS) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IL2 RMS",50318,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (RMS) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IL3 RMS",50320,2,"4","Float IEE754","Word 0","A","Messwert: Phasenstrom (RMS) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IE gem RMS",50322,2,"4","Float IEE754","Word 0","A","Messwert (gemessen): IE (RMS) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","IE err RMS",50324,2,"4","Float IEE754","Word 0","A","Messwert (errechnet): IE (RMS) , wie im Fehlerrekorder gespeichert"]
["StW - Fehlerwert","%(I2/I1)",50376,2,"4","Float IEE754","Word 0","%","Messwert (errechnet): I2/I1, Drehfeldrichtung wird automatisch berücksichtigt. , wie im Fehlerrekorder gespeichert"]
["Sync","f SS",20520,2,"4","Float IEE754","Word 0","Hz","Frequenz auf der Sammelschienenseite"]
["Sync","U SS",20522,2,"4","Float IEE754","Word 0","V","Spannung auf der Sammelschiene"]
["Sync","SS Winkel",20524,2,"4","Float IEE754","Word 0","°","Winkel der Referenzspannung"]
["Sync","delta Winkel",20526,2,"4","Float IEE754","Word 0","°","Differenzwinkel zwischen Sammelschiene und Netzspannung."]
["Sync","delta U",20528,2,"4","Float IEE754","Word 0","V","Spannungsdifferenz zwischen Netz und Sammelschiene."]
["Sync","f Netz",20530,2,"4","Float IEE754","Word 0","Hz","Frequenz auf der Netzseite"]
["Sync","U Netz",20532,2,"4","Float IEE754","Word 0","V","Netzspannung"]
["Sync","Netz Winkel",20534,2,"4","Float IEE754","Word 0","°","Winkel der Netzspannung"]
["Sync","delta f",20536,2,"4","Float IEE754","Word 0","Hz","Schlupffrequenz"]
["ThA","Therm. Niveau",20110,2,"4","Float IEE754","Word 0","%","Messwert: Aktuelles Thermisches Niveau"]
["ThA","Zeit bis zur Auslösung",20112,2,"4","Float IEE754","Word 0","s","Messwert (berechnet/gemessen): Noch verbleibende Zeit bis zur Auslösung der thermischen Überlastfunktion"]
["ThA","Therm Kap max",21086,2,"4","Float IEE754","Word 0","%","Therm Kap  Maximalwert"]
["ThA - Fehlerwert","Therm. Niveau",50110,2,"4","Float IEE754","Word 0","%","Messwert: Aktuelles Thermisches Niveau , wie im Fehlerrekorder gespeichert"]
["ThA - Fehlerwert","Zeit bis zur Auslösung",50112,2,"4","Float IEE754","Word 0","s","Messwert (berechnet/gemessen): Noch verbleibende Zeit bis zur Auslösung der thermischen Überlastfunktion , wie im Fehlerrekorder gespeichert"]
["Werte","Build",20008,2,"4","Float IEE754","Word 0","-","Build-Nummer"]
["Werte","Betriebsstunden Z",20010,2,"4","Float IEE754","Word 0","h","Betriebsstunden Zähler des Schutzgeräts"]

{"sheet":"causeOfTrip","index":5,"n_rows":61,"n_cols":3,"rows_kept":61,"cut":false,"hidden":false,"merged":[]}
["COT modules","COT Code","COT description"]
[null,1,"NORM"]
["AnaP[1]",1001]
["AnaP[2]",1002]
["AnaP[3]",1003]
["AnaP[4]",1004]
["IE[1]",1201]
["IE[2]",1202]
["IE[3]",1203]
["IE[4]",1204]
["ExS[1]",1306]
["ExS[2]",1307]
["ExS[3]",1308]
["ExS[4]",1309]
["LS-Mitnahme",1310]
["f[1]",1401]
["f[2]",1402]
["f[3]",1403]
["f[4]",1404]
["f[5]",1405]
["f[6]",1406]
["df/dt",1407]
["delta phi",1408]
["LVRT[1]",2501]
["LVRT[2]",2502]
["I2>[1]",2901]
["I2>[2]",2902]
["U012[1]",3001]
["U012[2]",3002]
["U012[3]",3003]
["U012[4]",3004]
["U012[5]",3005]
["U012[6]",3006]
["I[1]",3201]
["I[2]",3202]
["I[3]",3203]
["I[4]",3204]
["I[5]",3205]
["I[6]",3206]
["PQS[1]",3401]
["PQS[2]",3402]
["PQS[3]",3403]
["PQS[4]",3404]
["PQS[5]",3405]
["PQS[6]",3406]
["P",3407]
["Q",3408]
["LF[1]",3501]
["LF[2]",3502]
["Q->&U<",3601]
["ThA",3801]
["UE[1]",4001]
["UE[2]",4002]
["U[1]",4101]
["U[2]",4102]
["U[3]",4103]
["U[4]",4104]
["U[5]",4105]
["U[6]",4106]
["HVRT[1]",4107]
["HVRT[2]",4108]