{"text_format":"2","workbook":"xlsx","n_sheets":6,"sheets":["Version","State","Adjust","Command","Measure","causeOfTrip"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Version","index":0,"n_rows":2,"n_cols":2,"rows_kept":2,"cut":false,"hidden":false,"merged":[]}
["Handoff","SW-Version"]
[47458,"3.7.b"]

{"sheet":"State","index":1,"n_rows":1382,"n_cols":9,"rows_kept":1382,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["AR","actif",46,1,"3","Bit","0x1","-","Signal : actif"]
["AR","ExBlo",46,1,"3","Bit","0x2","-","Signal : Blocage externe"]
["AR","exéc.",46,1,"3","Bit","0x8","-","Signal : Réenclenchement automatique en cours"]
["AR","t-mor",46,1,"3","Bit","0x10","-","Signal : Temps mort entre le déclenchement et la tentative de réenclenchement"]
["AR","réussi (*)",46,1,"3","Bit","0x100","-","Signal : Réenclenchement automatique réussi"]
["AR","échec (*)",46,1,"3","Bit","0x200","-","Signal : Échec de réenclenchement automatique"]
["AR","Surv t-RA",46,1,"3","Bit","0x1000","-","Signal :  Surveillance réenclenchement automatique"]
["AR","ExBlo1-I",47,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["AR","ExBlo2-I",47,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["AR","Cmd CB ON",47,1,"3","Bit","0x10","-","Signal : Commande d'activation (ON) d'un disjoncteur"]
["AR","Av impul (*)",47,1,"3","Bit","0x20","-","Commande avant impulsion"]
["AR","Impl 1 (*)",47,1,"3","Bit","0x40","-","Commande d'impulsion"]
["AR","Impl 2 (*)",47,1,"3","Bit","0x80","-","Commande d'impulsion"]
["AR","Impl 3 (*)",47,1,"3","Bit","0x100","-","Commande d'impulsion"]
["AR","Impl 4 (*)",47,1,"3","Bit","0x200","-","Commande d'impulsion"]
["AR","Impl 5 (*)",47,1,"3","Bit","0x400","-","Commande d'impulsion"]
["AR","Impl 6 (*)",47,1,"3","Bit","0x800","-","Commande d'impulsion"]
["AR","Ex verr-I",156,1,"3","Bit","0x1","-","État d'entrée d'un module : Verrouillage externe de réenclenchement automatique."]
["AR","Ex imp Inc-I",156,1,"3","Bit","0x2","-","État d'entrée d'un module : Ce signal externe incrémente le compteur d'impulsions de réenclenchement automatique. Cela peut s'utiliser pour la coordination des zones (des modules de réenclenchement automatique en amont). Remarques: ce paramètre active uniquement cette fonctionnalité. L'affectation doit être configurée dans les paramètres globaux."]
["AR","Blo",156,1,"3","Bit","0x4","-","Signal : Le réenclenchement automatique est bloqué"]
["AR","t-Blo apr CB man ON",156,1,"3","Bit","0x8","-","Signal : Réenclenchement automatique bloqué après action manuelle sur le disjoncteur. Cette temporisation est activée si le disjoncteur est actionné manuellement. Lorsque cette temporisation est en cours d'exécution, le réenclenchement automatique ne peut pas être activé."]
["AR","Verr",156,1,"3","Bit","0x10","-","Signal : Le réenclenchement automatique est verrouillé"]
["AR","t-réin verr",156,1,"3","Bit","0x20","-","Signal : Temporisation pour la réinitialisation du verrouillage du réenclenchement automatique. La réinitialisation du réenclenchement automatique est retardée de cette durée après la détection du signal de réinitialisation (entrée numérique ou Scada)."]
["AR","Prêt",156,1,"3","Bit","0x40","-","Signal : Prêt à réenclencher"]
["AR","t-Run2Ready",156,1,"3","Bit","0x80","-","Signal :  Temps d'examen : si le disjoncteur reste en position fermée après une tentative de réenclenchement pendant la durée de cette temporisation, le réenclenchement automatique est réussi ; le module de réenclenchement automatique revient dans l'état 'Prêt'."]
["AR","Attente",156,1,"3","Bit","0x100","-","Signal : Attente"]
["AR","Alar. maint. 1",156,1,"3","Bit","0x200","-","Signal : Réenclenchement automatique - Alarme de maintenance 1 ; trop d'opérations de commutation"]
["AR","Alar. maint. 2",156,1,"3","Bit","0x400","-","Signal : Réenclenchement automatique - Alarme de maintenance 2 ; trop d'opérations de commutation"]
["AR","Max impuls / h dépass",156,1,"3","Bit","0x800","-","Signal : Le nombre maximal d'impulsions autorisé par heure est dépassé."]
["AnIn[1]","Rupture fil",247,1,"3","Bit","0x1","-","Signal : Rupture d'un fil. Ce signal est valide uniquement si l'entrée analogique est utilisée en mode 4...20 mA."]
["AnIn[1]","Entr forcée",247,1,"3","Bit","0x2","-","La valeur de l'entrée analogique a été forcée. Cela signifie que la valeur de l'entrée analogique est forcée et ne représente pas la valeur réelle mesurée."]
["AnIn[2]","Rupture fil",248,1,"3","Bit","0x4","-","Signal : Rupture d'un fil. Ce signal est valide uniquement si l'entrée analogique est utilisée en mode 4...20 mA."]
["AnIn[2]","Entr forcée",248,1,"3","Bit","0x8","-","La valeur de l'entrée analogique a été forcée. Cela signifie que la valeur de l'entrée analogique est forcée et ne représente pas la valeur réelle mesurée."]
["AnaP[1]","ExBlo1-I",224,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["AnaP[1]","ExBlo2-I",224,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["AnaP[1]","ExBlo TripCmd-I",224,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["AnaP[1]","actif",224,1,"3","Bit","0x8","-","Signal : actif"]
["AnaP[1]","ExBlo",224,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["AnaP[1]","Blo TripCmd",224,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["AnaP[1]","ExBlo TripCmd",224,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["AnaP[1]","Excit",224,1,"3","Bit","0x80","-","Signal: Alarme d'entrée analogique"]
["AnaP[1]","Décl (*)",224,1,"3","Bit","0x100","-","Signal : Décl"]
["AnaP[1]","TripCmd (*)",224,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["AnaP[2]","ExBlo1-I",225,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["AnaP[2]","ExBlo2-I",225,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["AnaP[2]","ExBlo TripCmd-I",225,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["AnaP[2]","actif",225,1,"3","Bit","0x8","-","Signal : actif"]
["AnaP[2]","ExBlo",225,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["AnaP[2]","Blo TripCmd",225,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["AnaP[2]","ExBlo TripCmd",225,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["AnaP[2]","Excit",225,1,"3","Bit","0x80","-","Signal: Alarme d'entrée analogique"]
["AnaP[2]","Décl (*)",225,1,"3","Bit","0x100","-","Signal : Décl"]
["AnaP[2]","TripCmd (*)",225,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["AnaP[3]","ExBlo1-I",226,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["AnaP[3]","ExBlo2-I",226,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["AnaP[3]","ExBlo TripCmd-I",226,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["AnaP[3]","actif",226,1,"3","Bit","0x8","-","Signal : actif"]
["AnaP[3]","ExBlo",226,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["AnaP[3]","Blo TripCmd",226,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["AnaP[3]","ExBlo TripCmd",226,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["AnaP[3]","Excit",226,1,"3","Bit","0x80","-","Signal: Alarme d'entrée analogique"]
["AnaP[3]","Décl (*)",226,1,"3","Bit","0x100","-","Signal : Décl"]
["AnaP[3]","TripCmd (*)",226,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["AnaP[4]","ExBlo1-I",227,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["AnaP[4]","ExBlo2-I",227,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["AnaP[4]","ExBlo TripCmd-I",227,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["AnaP[4]","actif",227,1,"3","Bit","0x8","-","Signal : actif"]
["AnaP[4]","ExBlo",227,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["AnaP[4]","Blo TripCmd",227,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["AnaP[4]","ExBlo TripCmd",227,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["AnaP[4]","Excit",227,1,"3","Bit","0x80","-","Signal: Alarme d'entrée analogique"]
["AnaP[4]","Décl (*)",227,1,"3","Bit","0x100","-","Signal : Décl"]
["AnaP[4]","TripCmd (*)",227,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["CBF","ExBlo1-I",53,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["CBF","ExBlo2-I",53,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["CBF","actif",53,1,"3","Bit","0x4","-","Signal : actif"]
["CBF","ExBlo",53,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["CBF","Décl1-I",53,1,"3","Bit","0x10","-","Entrée d'un module : Déclencheur qui active le défaut de disjoncteur (CBF)"]
["CBF","Décl2-I",53,1,"3","Bit","0x20","-","Entrée d'un module : Déclencheur qui active le défaut de disjoncteur (CBF)"]
["CBF","Décl3-I",53,1,"3","Bit","0x40","-","Entrée d'un module : Déclencheur qui active le défaut de disjoncteur (CBF)"]
["CBF","exéc.",53,1,"3","Bit","0x80","-","Signal : CBF (Défaut disjoncteur) -Module activé"]
["CBF","Alarm (*)",53,1,"3","Bit","0x100","-","Signal : Défaut de disjoncteur"]
["CBF","Verr (*)",53,1,"3","Bit","0x200","-","Signal: Verr"]
["CBF","En attente de décl. (*)",53,1,"3","Bit","0x400","-","En attente de décl."]
["CLPU","ExBlo1-I",66,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["CLPU","ExBlo2-I",66,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["CLPU","Ex rev Interl-I",66,1,"3","Bit","0x4","-","État d'entrée d'un module : Verrouillage externe"]
["CLPU","actif",66,1,"3","Bit","0x8","-","Signal : actif"]
["CLPU","ExBlo",66,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["CLPU","Ex rev Interl",66,1,"3","Bit","0x20","-","Signal : Verrouillage externe"]
["CLPU","activé",66,1,"3","Bit","0x200","-","Signal : Charge froide activée"]
["CLPU","détecté (*)",66,1,"3","Bit","0x400","-","Signal : Charge froide détectée"]
["CLPU","I<",66,1,"3","Bit","0x800","-","Signal : Pas de courant de charge."]
["CLPU","Blo RA",66,1,"3","Bit","0x1000","-","Signal : Bloqué par le réenclenchement automatique"]
["CLPU","Ap cou char",66,1,"3","Bit","0x2000","-","Signal : Appel de courant de la charge"]
["CLPU","Tps établis",66,1,"3","Bit","0x4000","-","Signal :  Temps d'établissement"]
["CTS","ExBlo1-I",137,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["CTS","ExBlo2-I",137,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["CTS","actif",137,1,"3","Bit","0x4","-","Signal : actif"]
["CTS","ExBlo",137,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["CTS","Alarm",137,1,"3","Bit","0x10","-","Signal : Alarme de surveillance du circuit de mesure d'un transformateur de courant"]
["Contac PSet","PS 1",59,1,"3","Bit","0x1","-","Signal: Le groupe de paramètres actuellement actif est le groupe PS. 1"]
["Contac PSet","PS 2",59,1,"3","Bit","0x2","-","Signal: Le groupe de paramètres actuellement actif est le groupe PS. 2"]
["Contac PSet","PS 3",59,1,"3","Bit","0x4","-","Signal: Le groupe de paramètres actuellement actif est le groupe PS. 3"]
["Contac PSet","PS 4",59,1,"3","Bit","0x8","-","Signal: Le groupe de paramètres actuellement actif est le groupe PS. 4"]
["Contac PSet","PSS manuel",59,1,"3","Bit","0x10","-","Signal: Commutation manuelle d'un groupe de paramètres"]
["Contac PSet","PSS via Scada",59,1,"3","Bit","0x20","-","Signal: Commutation de groupe de paramètres via le système Scada. Écrivez sur cet octet de sortie le nombre entier correspondant au groupe de paramètres qui doit devenir actif (par ex. : 4 => commutation vers le groupe de paramètres 4)."]
["Contac PSet","PSS via ent fct",59,1,"3","Bit","0x40","-","Signal: Commutation de groupe de paramètres via une fonction d'entrée"]
["Contac PSet","PS1-I",59,1,"3","Bit","0x80","-","État d'entrée du module respectivement du signal qui doit activer cette configuration."]
["Contac PSet","PS2-I",59,1,"3","Bit","0x100","-","État d'entrée du module respectivement du signal qui doit activer cette configuration."]
["Contac PSet","PS3-I",59,1,"3","Bit","0x200","-","État d'entrée du module respectivement du signal qui doit activer cette configuration."]
["Contac PSet","PS4-I",59,1,"3","Bit","0x400","-","État d'entrée du module respectivement du signal qui doit activer cette configuration."]
["Contac PSet","min 1 param modif (*)",59,1,"3","Bit","0x800","-","Signal: Au moins un paramètre a été modifié"]
["Ctrl","Local",176,1,"3","Bit","0x1","-","Autorisation de commutation : Local"]
["Ctrl","Dist",176,1,"3","Bit","0x2","-","Autorisation de commutation : Distant"]
["Ctrl","NonInterl",176,1,"3","Bit","0x4","-","L'absence de blocage est active"]
["Ctrl","Perturbation SG",176,1,"3","Bit","0x8","-","(Au moins un) appareillage de connexion présente une perturbation."]
["Ctrl","SG indéterminé",176,1,"3","Bit","0x10","-","(Au moins un) appareillage de connexion est mobile (sa position ne peut pas être déterminée)."]
["Empl EN X1","EN 1",1000,1,"3","Bit","0x1","-","Signal : Entrée numérique"]
["Empl EN X1","EN 2",1000,1,"3","Bit","0x2","-","Signal : Entrée numérique"]
["Empl EN X1","EN 3",1000,1,"3","Bit","0x4","-","Signal : Entrée numérique"]
["Empl EN X1","EN 4",1000,1,"3","Bit","0x8","-","Signal : Entrée numérique"]
["Empl EN X1","EN 5",1000,1,"3","Bit","0x10","-","Signal : Entrée numérique"]
["Empl EN X1","EN 6",1000,1,"3","Bit","0x20","-","Signal : Entrée numérique"]
["Empl EN X1","EN 7",1000,1,"3","Bit","0x40","-","Signal : Entrée numérique"]
["Empl EN X1","EN 8",1000,1,"3","Bit","0x80","-","Signal : Entrée numérique"]
["Empl EN X5","EN 1",1014,1,"3","Bit","0x1","-","Signal : Entrée numérique"]
["Empl EN X5","EN 2",1014,1,"3","Bit","0x2","-","Signal : Entrée numérique"]
["Empl EN X5","EN 3",1014,1,"3","Bit","0x4","-","Signal : Entrée numérique"]
["Empl EN X5","EN 4",1014,1,"3","Bit","0x8","-","Signal : Entrée numérique"]
["Empl EN X5","EN 5",1014,1,"3","Bit","0x10","-","Signal : Entrée numérique"]
["Empl EN X5","EN 6",1014,1,"3","Bit","0x20","-","Signal : Entrée numérique"]
["Empl EN X5","EN 7",1014,1,"3","Bit","0x40","-","Signal : Entrée numérique"]
["Empl EN X5","EN 8",1014,1,"3","Bit","0x80","-","Signal : Entrée numérique"]
["Empl EN X6","EN 1",1001,1,"3","Bit","0x1","-","Signal : Entrée numérique"]
["Empl EN X6","EN 2",1001,1,"3","Bit","0x2","-","Signal : Entrée numérique"]
["Empl EN X6","EN 3",1001,1,"3","Bit","0x4","-","Signal : Entrée numérique"]
["Empl EN X6","EN 4",1001,1,"3","Bit","0x8","-","Signal : Entrée numérique"]
["Empl EN X6","EN 5",1001,1,"3","Bit","0x10","-","Signal : Entrée numérique"]
["Empl EN X6","EN 6",1001,1,"3","Bit","0x20","-","Signal : Entrée numérique"]
["Empl EN X6","EN 7",1001,1,"3","Bit","0x40","-","Signal : Entrée numérique"]
["Empl EN X6","EN 8",1001,1,"3","Bit","0x80","-","Signal : Entrée numérique"]
["Empl SB X2","SB 1",1003,1,"3","Bit","0x1","-","Signal : Relais de sortie binaire"]
["Empl SB X2","SB 2",1003,1,"3","Bit","0x2","-","Signal : Relais de sortie binaire"]
["Empl SB X2","SB 3",1003,1,"3","Bit","0x4","-","Signal : Relais de sortie binaire"]
["Empl SB X2","SB 4",1003,1,"3","Bit","0x8","-","Signal : Relais de sortie binaire"]
["Empl SB X2","SB 5",1003,1,"3","Bit","0x10","-","Signal : Relais de sortie binaire"]
["Empl SB X2","SB 6",1003,1,"3","Bit","0x20","-","Signal : Relais de sortie binaire"]
["Empl SB X2","DÉSARMÉ!",1003,1,"3","Bit","0x40","-","Signal : ATTENT! RELAIS DÉSARMÉS afin d'effectuer la maintenance en sécurité en éliminant le risque de déconnecter un processus complet. (Remarque : il n'est pas possible de désarmer le contact d'auto-surveillance). VOUS DEVEZ VÉRIFIER que les relais sont RÉARMÉS après la maintenance"]
["Empl SB X2","Sorts forcé",1003,1,"3","Bit","0x80","-","Signal : L'état d'au moins une sortie relais a été forcé. Cela signifie que l'état d'au moins un relais est forcé et n'indique donc pas l'état des signaux affectés."]
["Empl SB X4","SB 1",1015,1,"3","Bit","0x1","-","Signal : Relais de sortie binaire"]
["Empl SB X4","SB 2",1015,1,"3","Bit","0x2","-","Signal : Relais de sortie binaire"]
["Empl SB X4","SB 3",1015,1,"3","Bit","0x4","-","Signal : Relais de sortie binaire"]
["Empl SB X4","SB 4",1015,1,"3","Bit","0x8","-","Signal : Relais de sortie binaire"]
["Empl SB X4","SB 5",1015,1,"3","Bit","0x10","-","Signal : Relais de sortie binaire"]
["Empl SB X4","DÉSARMÉ!",1015,1,"3","Bit","0x40","-","Signal : ATTENT! RELAIS DÉSARMÉS afin d'effectuer la maintenance en sécurité en éliminant le risque de déconnecter un processus complet. (Remarque : il n'est pas possible de désarmer le contact d'auto-surveillance). VOUS DEVEZ VÉRIFIER que les relais sont RÉARMÉS après la maintenance"]
["Empl SB X4","Sorts forcé",1015,1,"3","Bit","0x80","-","Signal : L'état d'au moins une sortie relais a été forcé. Cela signifie que l'état d'au moins un relais est forcé et n'indique donc pas l'état des signaux affectés."]
["Empl SB X5","SB 1",1004,1,"3","Bit","0x1","-","Signal : Relais de sortie binaire"]
["Empl SB X5","SB 2",1004,1,"3","Bit","0x2","-","Signal : Relais de sortie binaire"]
["Empl SB X5","SB 3",1004,1,"3","Bit","0x4","-","Signal : Relais de sortie binaire"]
["Empl SB X5","SB 4",1004,1,"3","Bit","0x8","-","Signal : Relais de sortie binaire"]
["Empl SB X5","SB 5",1004,1,"3","Bit","0x10","-","Signal : Relais de sortie binaire"]
["Empl SB X5","SB 6",1004,1,"3","Bit","0x20","-","Signal : Relais de sortie binaire"]
["Empl SB X5","DÉSARMÉ!",1004,1,"3","Bit","0x40","-","Signal : ATTENT! RELAIS DÉSARMÉS afin d'effectuer la maintenance en sécurité en éliminant le risque de déconnecter un processus complet. (Remarque : il n'est pas possible de désarmer le contact d'auto-surveillance). VOUS DEVEZ VÉRIFIER que les relais sont RÉARMÉS après la maintenance"]
["Empl SB X5","Sorts forcé",1004,1,"3","Bit","0x80","-","Signal : L'état d'au moins une sortie relais a été forcé. Cela signifie que l'état d'au moins un relais est forcé et n'indique donc pas l'état des signaux affectés."]
["Empl SB X5","SB 1",1013,1,"3","Bit","0x1","-","Signal : Relais de sortie binaire"]
["Empl SB X5","SB 2",1013,1,"3","Bit","0x2","-","Signal : Relais de sortie binaire"]
["Empl SB X5","SB 3",1013,1,"3","Bit","0x4","-","Signal : Relais de sortie binaire"]
["Empl SB X5","SB 4",1013,1,"3","Bit","0x8","-","Signal : Relais de sortie binaire"]
["Empl SB X5","DÉSARMÉ!",1013,1,"3","Bit","0x40","-","Signal : ATTENT! RELAIS DÉSARMÉS afin d'effectuer la maintenance en sécurité en éliminant le risque de déconnecter un processus complet. (Remarque : il n'est pas possible de désarmer le contact d'auto-surveillance). VOUS DEVEZ VÉRIFIER que les relais sont RÉARMÉS après la maintenance"]
["Empl SB X5","Sorts forcé",1013,1,"3","Bit","0x80","-","Signal : L'état d'au moins une sortie relais a été forcé. Cela signifie que l'état d'au moins un relais est forcé et n'indique donc pas l'état des signaux affectés."]
["Empl SB X6","SB 1",1016,1,"3","Bit","0x1","-","Signal : Relais de sortie binaire"]
["Empl SB X6","SB 2",1016,1,"3","Bit","0x2","-","Signal : Relais de sortie binaire"]
["Empl SB X6","SB 3",1016,1,"3","Bit","0x4","-","Signal : Relais de sortie binaire"]
["Empl SB X6","SB 4",1016,1,"3","Bit","0x8","-","Signal : Relais de sortie binaire"]
["Empl SB X6","DÉSARMÉ!",1016,1,"3","Bit","0x40","-","Signal : ATTENT! RELAIS DÉSARMÉS afin d'effectuer la maintenance en sécurité en éliminant le risque de déconnecter un processus complet. (Remarque : il n'est pas possible de désarmer le contact d'auto-surveillance). VOUS DEVEZ VÉRIFIER que les relais sont RÉARMÉS après la maintenance"]
["Empl SB X6","Sorts forcé",1016,1,"3","Bit","0x80","-","Signal : L'état d'au moins une sortie relais a été forcé. Cela signifie que l'état d'au moins un relais est forcé et n'indique donc pas l'état des signaux affectés."]
["ExP[1]","ExBlo1-I",49,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["ExP[1]","ExBlo2-I",49,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["ExP[1]","ExBlo TripCmd-I",49,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["ExP[1]","Alarm-I",49,1,"3","Bit","0x8","-","État d'entrée d'un module : Alarme"]
["ExP[1]","Décl-I",49,1,"3","Bit","0x10","-","État d'entrée d'un module : Décl"]
["ExP[1]","actif",49,1,"3","Bit","0x20","-","Signal : actif"]
["ExP[1]","ExBlo",49,1,"3","Bit","0x40","-","Signal : Blocage externe"]
["ExP[1]","Blo TripCmd",49,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["ExP[1]","ExBlo TripCmd",49,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["ExP[1]","Alarm",49,1,"3","Bit","0x200","-","Signal : Alarme"]
["ExP[1]","Décl (*)",49,1,"3","Bit","0x400","-","Signal : Décl"]
["ExP[1]","TripCmd (*)",49,1,"3","Bit","0x800","-","Signal : Commande de déclenchement"]
["ExP[2]","ExBlo1-I",50,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["ExP[2]","ExBlo2-I",50,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["ExP[2]","ExBlo TripCmd-I",50,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["ExP[2]","Alarm-I",50,1,"3","Bit","0x8","-","État d'entrée d'un module : Alarme"]
["ExP[2]","Décl-I",50,1,"3","Bit","0x10","-","État d'entrée d'un module : Décl"]
["ExP[2]","actif",50,1,"3","Bit","0x20","-","Signal : actif"]
["ExP[2]","ExBlo",50,1,"3","Bit","0x40","-","Signal : Blocage externe"]
["ExP[2]","Blo TripCmd",50,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["ExP[2]","ExBlo TripCmd",50,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["ExP[2]","Alarm",50,1,"3","Bit","0x200","-","Signal : Alarme"]
["ExP[2]","Décl (*)",50,1,"3","Bit","0x400","-","Signal : Décl"]
["ExP[2]","TripCmd (*)",50,1,"3","Bit","0x800","-","Signal : Commande de déclenchement"]
["ExP[3]","ExBlo1-I",51,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["ExP[3]","ExBlo2-I",51,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["ExP[3]","ExBlo TripCmd-I",51,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["ExP[3]","Alarm-I",51,1,"3","Bit","0x8","-","État d'entrée d'un module : Alarme"]
["ExP[3]","Décl-I",51,1,"3","Bit","0x10","-","État d'entrée d'un module : Décl"]
["ExP[3]","actif",51,1,"3","Bit","0x20","-","Signal : actif"]
["ExP[3]","ExBlo",51,1,"3","Bit","0x40","-","Signal : Blocage externe"]
["ExP[3]","Blo TripCmd",51,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["ExP[3]","ExBlo TripCmd",51,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["ExP[3]","Alarm",51,1,"3","Bit","0x200","-","Signal : Alarme"]
["ExP[3]","Décl (*)",51,1,"3","Bit","0x400","-","Signal : Décl"]
["ExP[3]","TripCmd (*)",51,1,"3","Bit","0x800","-","Signal : Commande de déclenchement"]
["ExP[4]","ExBlo1-I",52,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["ExP[4]","ExBlo2-I",52,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["ExP[4]","ExBlo TripCmd-I",52,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["ExP[4]","Alarm-I",52,1,"3","Bit","0x8","-","État d'entrée d'un module : Alarme"]
["ExP[4]","Décl-I",52,1,"3","Bit","0x10","-","État d'entrée d'un module : Décl"]
["ExP[4]","actif",52,1,"3","Bit","0x20","-","Signal : actif"]
["ExP[4]","ExBlo",52,1,"3","Bit","0x40","-","Signal : Blocage externe"]
["ExP[4]","Blo TripCmd",52,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["ExP[4]","ExBlo TripCmd",52,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["ExP[4]","Alarm",52,1,"3","Bit","0x200","-","Signal : Alarme"]
["ExP[4]","Décl (*)",52,1,"3","Bit","0x400","-","Signal : Décl"]
["ExP[4]","TripCmd (*)",52,1,"3","Bit","0x800","-","Signal : Commande de déclenchement"]
["HVRT[1]","ExBlo1-I",298,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["HVRT[1]","ExBlo2-I",298,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["HVRT[1]","ExBlo TripCmd-I",298,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["HVRT[1]","actif",298,1,"3","Bit","0x8","-","Signal : actif"]
["HVRT[1]","ExBlo",298,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["HVRT[1]","Alarm",298,1,"3","Bit","0x20","-","Signal : Alarme de l'étage de tension"]
["HVRT[1]","Alar. L1",298,1,"3","Bit","0x40","-","Signal : Alarme L1"]
["HVRT[1]","Alar. L2",298,1,"3","Bit","0x80","-","Signal : Alarme L2"]
["HVRT[1]","Alar. L3",298,1,"3","Bit","0x100","-","Signal : Alarme L3"]
["HVRT[1]","Décl (*)",298,1,"3","Bit","0x200","-","Signal : Décl"]
["HVRT[1]","Déc. L1 (*)",298,1,"3","Bit","0x400","-","Signal : Déclenchement général phase L1"]
["HVRT[1]","Déc. L2 (*)",298,1,"3","Bit","0x800","-","Signal : Déclenchement général phase L2"]
["HVRT[1]","Déc. L3 (*)",298,1,"3","Bit","0x1000","-","Signal : Déclenchement général phase L3"]
["HVRT[1]","TripCmd (*)",298,1,"3","Bit","0x2000","-","Signal : Commande de déclenchement"]
["HVRT[1]","Blo TripCmd",298,1,"3","Bit","0x4000","-","Signal : Commande de déclenchement bloquée"]
["HVRT[1]","ExBlo TripCmd",298,1,"3","Bit","0x8000","-","Signal : Blocage externe de la commande de déclenchement"]
["HVRT[2]","ExBlo1-I",299,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["HVRT[2]","ExBlo2-I",299,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["HVRT[2]","ExBlo TripCmd-I",299,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["HVRT[2]","actif",299,1,"3","Bit","0x8","-","Signal : actif"]
["HVRT[2]","ExBlo",299,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["HVRT[2]","Alarm",299,1,"3","Bit","0x20","-","Signal : Alarme de l'étage de tension"]
["HVRT[2]","Alar. L1",299,1,"3","Bit","0x40","-","Signal : Alarme L1"]
["HVRT[2]","Alar. L2",299,1,"3","Bit","0x80","-","Signal : Alarme L2"]
["HVRT[2]","Alar. L3",299,1,"3","Bit","0x100","-","Signal : Alarme L3"]
["HVRT[2]","Décl (*)",299,1,"3","Bit","0x200","-","Signal : Décl"]
["HVRT[2]","Déc. L1 (*)",299,1,"3","Bit","0x400","-","Signal : Déclenchement général phase L1"]
["HVRT[2]","Déc. L2 (*)",299,1,"3","Bit","0x800","-","Signal : Déclenchement général phase L2"]
["HVRT[2]","Déc. L3 (*)",299,1,"3","Bit","0x1000","-","Signal : Déclenchement général phase L3"]
["HVRT[2]","TripCmd (*)",299,1,"3","Bit","0x2000","-","Signal : Commande de déclenchement"]
["HVRT[2]","Blo TripCmd",299,1,"3","Bit","0x4000","-","Signal : Commande de déclenchement bloquée"]
["HVRT[2]","ExBlo TripCmd",299,1,"3","Bit","0x8000","-","Signal : Blocage externe de la commande de déclenchement"]
["I2>[1]","ExBlo1-I",82,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["I2>[1]","ExBlo2-I",82,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["I2>[1]","ExBlo TripCmd-I",82,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["I2>[1]","actif",82,1,"3","Bit","0x8","-","Signal : actif"]
["I2>[1]","ExBlo",82,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["I2>[1]","Blo TripCmd",82,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["I2>[1]","ExBlo TripCmd",82,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["I2>[1]","Alarm",82,1,"3","Bit","0x80","-","Signal : Alarme de composante inverse"]
["I2>[1]","Décl (*)",82,1,"3","Bit","0x100","-","Signal : Décl"]
["I2>[1]","TripCmd (*)",82,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["I2>[2]","ExBlo1-I",83,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["I2>[2]","ExBlo2-I",83,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["I2>[2]","ExBlo TripCmd-I",83,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["I2>[2]","actif",83,1,"3","Bit","0x8","-","Signal : actif"]
["I2>[2]","ExBlo",83,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["I2>[2]","Blo TripCmd",83,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["I2>[2]","ExBlo TripCmd",83,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["I2>[2]","Alarm",83,1,"3","Bit","0x80","-","Signal : Alarme de composante inverse"]
["I2>[2]","Décl (*)",83,1,"3","Bit","0x100","-","Signal : Décl"]
["I2>[2]","TripCmd (*)",83,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["IG[1]","ExBlo1-I",15,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["IG[1]","ExBlo2-I",15,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["IG[1]","ExBlo TripCmd-I",15,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["IG[1]","Ex rev Interl-I",15,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["IG[1]","actif",15,1,"3","Bit","0x10","-","Signal : actif"]
["IG[1]","ExBlo",15,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["IG[1]","Ex rev Interl",15,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["IG[1]","Blo TripCmd",15,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["IG[1]","ExBlo TripCmd",15,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["IG[1]","IGH2 Blo",15,1,"3","Bit","0x200","-","Signal : bloqué par un appel de courant"]
["IG[1]","Alarm",15,1,"3","Bit","0x400","-","Signal : seuil d'alarme dépassé"]
["IG[1]","Décl (*)",15,1,"3","Bit","0x800","-","Signal : Décl"]
["IG[1]","TripCmd (*)",15,1,"3","Bit","0x1000","-","Signal : Commande de déclenchement"]
["IG[2]","ExBlo1-I",16,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["IG[2]","ExBlo2-I",16,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["IG[2]","ExBlo TripCmd-I",16,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["IG[2]","Ex rev Interl-I",16,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["IG[2]","actif",16,1,"3","Bit","0x10","-","Signal : actif"]
["IG[2]","ExBlo",16,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["IG[2]","Ex rev Interl",16,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["IG[2]","Blo TripCmd",16,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["IG[2]","ExBlo TripCmd",16,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["IG[2]","IGH2 Blo",16,1,"3","Bit","0x200","-","Signal : bloqué par un appel de courant"]
["IG[2]","Alarm",16,1,"3","Bit","0x400","-","Signal : seuil d'alarme dépassé"]
["IG[2]","Décl (*)",16,1,"3","Bit","0x800","-","Signal : Décl"]
["IG[2]","TripCmd (*)",16,1,"3","Bit","0x1000","-","Signal : Commande de déclenchement"]
["IG[3]","ExBlo1-I",17,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["IG[3]","ExBlo2-I",17,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["IG[3]","ExBlo TripCmd-I",17,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["IG[3]","Ex rev Interl-I",17,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["IG[3]","actif",17,1,"3","Bit","0x10","-","Signal : actif"]
["IG[3]","ExBlo",17,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["IG[3]","Ex rev Interl",17,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["IG[3]","Blo TripCmd",17,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["IG[3]","ExBlo TripCmd",17,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["IG[3]","IGH2 Blo",17,1,"3","Bit","0x200","-","Signal : bloqué par un appel de courant"]
["IG[3]","Alarm",17,1,"3","Bit","0x400","-","Signal : seuil d'alarme dépassé"]
["IG[3]","Décl (*)",17,1,"3","Bit","0x800","-","Signal : Décl"]
["IG[3]","TripCmd (*)",17,1,"3","Bit","0x1000","-","Signal : Commande de déclenchement"]
["IG[4]","ExBlo1-I",18,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["IG[4]","ExBlo2-I",18,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["IG[4]","ExBlo TripCmd-I",18,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["IG[4]","Ex rev Interl-I",18,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["IG[4]","actif",18,1,"3","Bit","0x10","-","Signal : actif"]
["IG[4]","ExBlo",18,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["IG[4]","Ex rev Interl",18,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["IG[4]","Blo TripCmd",18,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["IG[4]","ExBlo TripCmd",18,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["IG[4]","IGH2 Blo",18,1,"3","Bit","0x200","-","Signal : bloqué par un appel de courant"]
["IG[4]","Alarm",18,1,"3","Bit","0x400","-","Signal : seuil d'alarme dépassé"]
["IG[4]","Décl (*)",18,1,"3","Bit","0x800","-","Signal : Décl"]
["IG[4]","TripCmd (*)",18,1,"3","Bit","0x1000","-","Signal : Commande de déclenchement"]
["IH2","ExBlo1-I",22,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["IH2","ExBlo2-I",22,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["IH2","actif",22,1,"3","Bit","0x4","-","Signal : actif"]
["IH2","ExBlo",22,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["IH2","Blo L1",22,1,"3","Bit","0x10","-","Signal : L1 bloquée"]
["IH2","Blo L2",22,1,"3","Bit","0x20","-","Signal : L2 bloquée"]
["IH2","Blo L3",22,1,"3","Bit","0x40","-","Signal : L3 bloquée"]
["IH2","Blo IG mes",22,1,"3","Bit","0x80","-","Signal : Blocage du module de protection à la terre (courant à la terre mesuré)"]
["IH2","3-ph Blo",22,1,"3","Bit","0x100","-","Signal : un appel de courant a été détecté sur au moins une phase. Commande de déclenchement bloquée."]
["IH2","Blo IG calc",22,1,"3","Bit","0x200","-","Signal : Blocage du module de protection à la terre (courant à la terre calculé)"]
["IRIG-B","IRIG-B Actif",148,1,"3","Bit","0x1","-","Signal: S'il n'y a pas de signal IRIG-B valide pendant 60 s, IRIG-B est considéré inactif."]
["IRIG-B","High-Low Invert",148,1,"3","Bit","0x2","-","Signal : les signaux Haut et BAS du IRIG-B sont inversés. Cela ne signifie PAS que le câblage est défaillant. Si le câblage est défaillant, aucun signal IRIG-B n'est détecté."]
["I[1]","ExBlo1-I",3,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["I[1]","ExBlo2-I",3,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["I[1]","ExBlo TripCmd-I",3,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["I[1]","Ex rev Interl-I",3,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["I[1]","actif",3,1,"3","Bit","0x10","-","Signal : actif"]
["I[1]","ExBlo",3,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["I[1]","Ex rev Interl",3,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["I[1]","Blo TripCmd",3,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["I[1]","ExBlo TripCmd",3,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["I[1]","IH2 Blo",3,1,"3","Bit","0x200","-","Signal : Blocage de la commande de déclenchement par un appel de courant"]
["I[1]","Alar. L1",4,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["I[1]","Alar. L2",4,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["I[1]","Alar. L3",4,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["I[1]","Alarm",4,1,"3","Bit","0x8","-","Signal : Alarme"]
["I[1]","Déc. L1 (*)",4,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["I[1]","Déc. L2 (*)",4,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["I[1]","Déc. L3 (*)",4,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["I[1]","Décl (*)",4,1,"3","Bit","0x80","-","Signal : Décl"]
["I[1]","TripCmd (*)",4,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["I[2]","ExBlo1-I",5,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["I[2]","ExBlo2-I",5,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["I[2]","ExBlo TripCmd-I",5,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["I[2]","Ex rev Interl-I",5,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["I[2]","actif",5,1,"3","Bit","0x10","-","Signal : actif"]
["I[2]","ExBlo",5,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["I[2]","Ex rev Interl",5,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["I[2]","Blo TripCmd",5,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["I[2]","ExBlo TripCmd",5,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["I[2]","IH2 Blo",5,1,"3","Bit","0x200","-","Signal : Blocage de la commande de déclenchement par un appel de courant"]
["I[2]","Alar. L1",6,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["I[2]","Alar. L2",6,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["I[2]","Alar. L3",6,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["I[2]","Alarm",6,1,"3","Bit","0x8","-","Signal : Alarme"]
["I[2]","Déc. L1 (*)",6,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["I[2]","Déc. L2 (*)",6,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["I[2]","Déc. L3 (*)",6,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["I[2]","Décl (*)",6,1,"3","Bit","0x80","-","Signal : Décl"]
["I[2]","TripCmd (*)",6,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["I[3]","ExBlo1-I",7,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["I[3]","ExBlo2-I",7,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["I[3]","ExBlo TripCmd-I",7,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["I[3]","Ex rev Interl-I",7,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["I[3]","actif",7,1,"3","Bit","0x10","-","Signal : actif"]
["I[3]","ExBlo",7,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["I[3]","Ex rev Interl",7,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["I[3]","Blo TripCmd",7,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["I[3]","ExBlo TripCmd",7,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["I[3]","IH2 Blo",7,1,"3","Bit","0x200","-","Signal : Blocage de la commande de déclenchement par un appel de courant"]
["I[3]","Alar. L1",8,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["I[3]","Alar. L2",8,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["I[3]","Alar. L3",8,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["I[3]","Alarm",8,1,"3","Bit","0x8","-","Signal : Alarme"]
["I[3]","Déc. L1 (*)",8,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["I[3]","Déc. L2 (*)",8,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["I[3]","Déc. L3 (*)",8,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["I[3]","Décl (*)",8,1,"3","Bit","0x80","-","Signal : Décl"]
["I[3]","TripCmd (*)",8,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["I[4]","ExBlo1-I",9,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["I[4]","ExBlo2-I",9,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["I[4]","ExBlo TripCmd-I",9,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["I[4]","Ex rev Interl-I",9,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["I[4]","actif",9,1,"3","Bit","0x10","-","Signal : actif"]
["I[4]","ExBlo",9,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["I[4]","Ex rev Interl",9,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["I[4]","Blo TripCmd",9,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["I[4]","ExBlo TripCmd",9,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["I[4]","IH2 Blo",9,1,"3","Bit","0x200","-","Signal : Blocage de la commande de déclenchement par un appel de courant"]
["I[4]","Alar. L1",10,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["I[4]","Alar. L2",10,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["I[4]","Alar. L3",10,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["I[4]","Alarm",10,1,"3","Bit","0x8","-","Signal : Alarme"]
["I[4]","Déc. L1 (*)",10,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["I[4]","Déc. L2 (*)",10,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["I[4]","Déc. L3 (*)",10,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["I[4]","Décl (*)",10,1,"3","Bit","0x80","-","Signal : Décl"]
["I[4]","TripCmd (*)",10,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["I[5]","ExBlo1-I",11,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["I[5]","ExBlo2-I",11,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["I[5]","ExBlo TripCmd-I",11,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["I[5]","Ex rev Interl-I",11,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["I[5]","actif",11,1,"3","Bit","0x10","-","Signal : actif"]
["I[5]","ExBlo",11,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["I[5]","Ex rev Interl",11,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["I[5]","Blo TripCmd",11,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["I[5]","ExBlo TripCmd",11,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["I[5]","IH2 Blo",11,1,"3","Bit","0x200","-","Signal : Blocage de la commande de déclenchement par un appel de courant"]
["I[5]","Alar. L1",12,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["I[5]","Alar. L2",12,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["I[5]","Alar. L3",12,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["I[5]","Alarm",12,1,"3","Bit","0x8","-","Signal : Alarme"]
["I[5]","Déc. L1 (*)",12,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["I[5]","Déc. L2 (*)",12,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["I[5]","Déc. L3 (*)",12,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["I[5]","Décl (*)",12,1,"3","Bit","0x80","-","Signal : Décl"]
["I[5]","TripCmd (*)",12,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["I[6]","ExBlo1-I",13,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["I[6]","ExBlo2-I",13,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["I[6]","ExBlo TripCmd-I",13,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["I[6]","Ex rev Interl-I",13,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["I[6]","actif",13,1,"3","Bit","0x10","-","Signal : actif"]
["I[6]","ExBlo",13,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["I[6]","Ex rev Interl",13,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["I[6]","Blo TripCmd",13,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["I[6]","ExBlo TripCmd",13,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["I[6]","IH2 Blo",13,1,"3","Bit","0x200","-","Signal : Blocage de la commande de déclenchement par un appel de courant"]
["I[6]","Alar. L1",14,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["I[6]","Alar. L2",14,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["I[6]","Alar. L3",14,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["I[6]","Alarm",14,1,"3","Bit","0x8","-","Signal : Alarme"]
["I[6]","Déc. L1 (*)",14,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["I[6]","Déc. L2 (*)",14,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["I[6]","Déc. L3 (*)",14,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["I[6]","Décl (*)",14,1,"3","Bit","0x80","-","Signal : Décl"]
["I[6]","TripCmd (*)",14,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["Interdéclenchement","ExBlo1-I",253,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["Interdéclenchement","ExBlo2-I",253,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["Interdéclenchement","ExBlo TripCmd-I",253,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["Interdéclenchement","Alarm-I",253,1,"3","Bit","0x8","-","État d'entrée d'un module : Alarme"]
["Interdéclenchement","Décl-I",253,1,"3","Bit","0x10","-","État d'entrée d'un module : Décl"]
["Interdéclenchement","actif",253,1,"3","Bit","0x20","-","Signal : actif"]
["Interdéclenchement","ExBlo",253,1,"3","Bit","0x40","-","Signal : Blocage externe"]
["Interdéclenchement","Blo TripCmd",253,1,"3","Bit","0x80","-","Signal : Commande de déclenchement bloquée"]
["Interdéclenchement","ExBlo TripCmd",253,1,"3","Bit","0x100","-","Signal : Blocage externe de la commande de déclenchement"]
["Interdéclenchement","Alarm",253,1,"3","Bit","0x200","-","Signal : Alarme"]
["Interdéclenchement","Décl (*)",253,1,"3","Bit","0x400","-","Signal : Décl"]
["Interdéclenchement","TripCmd (*)",253,1,"3","Bit","0x800","-","Signal : Commande de déclenchement"]
["LVRT[1]","ExBlo1-I",254,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["LVRT[1]","ExBlo2-I",254,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["LVRT[1]","ExBlo TripCmd-I",254,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["LVRT[1]","actif",254,1,"3","Bit","0x8","-","Signal : actif"]
["LVRT[1]","ExBlo",254,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["LVRT[1]","Blo TripCmd",254,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["LVRT[1]","ExBlo TripCmd",254,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["LVRT[1]","Alar. L1",255,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["LVRT[1]","Alar. L2",255,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["LVRT[1]","Alar. L3",255,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["LVRT[1]","Alarm",255,1,"3","Bit","0x8","-","Signal : Alarme de l'étage de tension"]
["LVRT[1]","Déc. L1 (*)",255,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["LVRT[1]","Déc. L2 (*)",255,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["LVRT[1]","Déc. L3 (*)",255,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["LVRT[1]","Décl (*)",255,1,"3","Bit","0x80","-","Signal : Décl"]
["LVRT[1]","TripCmd (*)",255,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["LVRT[1]","t-LVRT exéc (*)",255,1,"3","Bit","0x200","-","Signal: t-LVRT exéc"]
["LVRT[2]","ExBlo1-I",270,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["LVRT[2]","ExBlo2-I",270,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["LVRT[2]","ExBlo TripCmd-I",270,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["LVRT[2]","actif",270,1,"3","Bit","0x8","-","Signal : actif"]
["LVRT[2]","ExBlo",270,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["LVRT[2]","Blo TripCmd",270,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["LVRT[2]","ExBlo TripCmd",270,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["LVRT[2]","Alar. L1",271,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["LVRT[2]","Alar. L2",271,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["LVRT[2]","Alar. L3",271,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["LVRT[2]","Alarm",271,1,"3","Bit","0x8","-","Signal : Alarme de l'étage de tension"]
["LVRT[2]","Déc. L1 (*)",271,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["LVRT[2]","Déc. L2 (*)",271,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["LVRT[2]","Déc. L3 (*)",271,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["LVRT[2]","Décl (*)",271,1,"3","Bit","0x80","-","Signal : Décl"]
["LVRT[2]","TripCmd (*)",271,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["LVRT[2]","t-LVRT exéc (*)",271,1,"3","Bit","0x200","-","Signal: t-LVRT exéc"]
["Logiqu","LE1.Port Out",1100,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE1.Tempo exp",1100,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE1.Out",1100,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE1.Out inversé",1100,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE1.Port In1-I",1100,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE1.Port In2-I",1100,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE1.Port In3-I",1100,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE1.Port In4-I",1100,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE1.Réin mémor-I",1100,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE2.Port Out",1101,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE2.Tempo exp",1101,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE2.Out",1101,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE2.Out inversé",1101,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE2.Port In1-I",1101,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE2.Port In2-I",1101,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE2.Port In3-I",1101,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE2.Port In4-I",1101,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE2.Réin mémor-I",1101,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE3.Port Out",1102,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE3.Tempo exp",1102,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE3.Out",1102,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE3.Out inversé",1102,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE3.Port In1-I",1102,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE3.Port In2-I",1102,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE3.Port In3-I",1102,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE3.Port In4-I",1102,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE3.Réin mémor-I",1102,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE4.Port Out",1103,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE4.Tempo exp",1103,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE4.Out",1103,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE4.Out inversé",1103,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE4.Port In1-I",1103,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE4.Port In2-I",1103,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE4.Port In3-I",1103,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE4.Port In4-I",1103,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE4.Réin mémor-I",1103,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE5.Port Out",1104,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE5.Tempo exp",1104,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE5.Out",1104,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE5.Out inversé",1104,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE5.Port In1-I",1104,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE5.Port In2-I",1104,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE5.Port In3-I",1104,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE5.Port In4-I",1104,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE5.Réin mémor-I",1104,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE6.Port Out",1105,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE6.Tempo exp",1105,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE6.Out",1105,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE6.Out inversé",1105,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE6.Port In1-I",1105,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE6.Port In2-I",1105,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE6.Port In3-I",1105,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE6.Port In4-I",1105,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE6.Réin mémor-I",1105,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE7.Port Out",1106,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE7.Tempo exp",1106,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE7.Out",1106,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE7.Out inversé",1106,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE7.Port In1-I",1106,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE7.Port In2-I",1106,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE7.Port In3-I",1106,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE7.Port In4-I",1106,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE7.Réin mémor-I",1106,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE8.Port Out",1107,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE8.Tempo exp",1107,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE8.Out",1107,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE8.Out inversé",1107,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE8.Port In1-I",1107,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE8.Port In2-I",1107,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE8.Port In3-I",1107,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE8.Port In4-I",1107,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE8.Réin mémor-I",1107,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE9.Port Out",1108,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE9.Tempo exp",1108,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE9.Out",1108,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE9.Out inversé",1108,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE9.Port In1-I",1108,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE9.Port In2-I",1108,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE9.Port In3-I",1108,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE9.Port In4-I",1108,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE9.Réin mémor-I",1108,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE10.Port Out",1109,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE10.Tempo exp",1109,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE10.Out",1109,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE10.Out inversé",1109,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE10.Port In1-I",1109,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE10.Port In2-I",1109,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE10.Port In3-I",1109,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE10.Port In4-I",1109,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE10.Réin mémor-I",1109,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE11.Port Out",1110,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE11.Tempo exp",1110,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE11.Out",1110,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE11.Out inversé",1110,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE11.Port In1-I",1110,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE11.Port In2-I",1110,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE11.Port In3-I",1110,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE11.Port In4-I",1110,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE11.Réin mémor-I",1110,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE12.Port Out",1111,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE12.Tempo exp",1111,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE12.Out",1111,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE12.Out inversé",1111,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE12.Port In1-I",1111,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE12.Port In2-I",1111,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE12.Port In3-I",1111,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE12.Port In4-I",1111,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE12.Réin mémor-I",1111,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE13.Port Out",1112,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE13.Tempo exp",1112,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE13.Out",1112,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE13.Out inversé",1112,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE13.Port In1-I",1112,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE13.Port In2-I",1112,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE13.Port In3-I",1112,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE13.Port In4-I",1112,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE13.Réin mémor-I",1112,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE14.Port Out",1113,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE14.Tempo exp",1113,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE14.Out",1113,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE14.Out inversé",1113,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE14.Port In1-I",1113,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE14.Port In2-I",1113,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE14.Port In3-I",1113,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE14.Port In4-I",1113,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE14.Réin mémor-I",1113,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE15.Port Out",1114,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE15.Tempo exp",1114,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE15.Out",1114,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE15.Out inversé",1114,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE15.Port In1-I",1114,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE15.Port In2-I",1114,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE15.Port In3-I",1114,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE15.Port In4-I",1114,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE15.Réin mémor-I",1114,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE16.Port Out",1115,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE16.Tempo exp",1115,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE16.Out",1115,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE16.Out inversé",1115,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE16.Port In1-I",1115,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE16.Port In2-I",1115,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE16.Port In3-I",1115,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE16.Port In4-I",1115,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE16.Réin mémor-I",1115,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE17.Port Out",1116,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE17.Tempo exp",1116,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE17.Out",1116,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE17.Out inversé",1116,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE17.Port In1-I",1116,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE17.Port In2-I",1116,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE17.Port In3-I",1116,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE17.Port In4-I",1116,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE17.Réin mémor-I",1116,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE18.Port Out",1117,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE18.Tempo exp",1117,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE18.Out",1117,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE18.Out inversé",1117,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE18.Port In1-I",1117,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE18.Port In2-I",1117,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE18.Port In3-I",1117,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE18.Port In4-I",1117,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE18.Réin mémor-I",1117,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE19.Port Out",1118,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE19.Tempo exp",1118,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE19.Out",1118,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE19.Out inversé",1118,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE19.Port In1-I",1118,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE19.Port In2-I",1118,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE19.Port In3-I",1118,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE19.Port In4-I",1118,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE19.Réin mémor-I",1118,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Logiqu","LE20.Port Out",1119,1,"3","Bit","0x1","-","Signal : Sortie de la porte logique"]
["Logiqu","LE20.Tempo exp",1119,1,"3","Bit","0x2","-","Signal : Sortie de la temporisation"]
["Logiqu","LE20.Out",1119,1,"3","Bit","0x4","-","Signal : Sortie mémorisée (Q)"]
["Logiqu","LE20.Out inversé",1119,1,"3","Bit","0x8","-","Signal : Sortie mémorisée inversée (Q NOT)"]
["Logiqu","LE20.Port In1-I",1119,1,"3","Bit","0x10","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE20.Port In2-I",1119,1,"3","Bit","0x20","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE20.Port In3-I",1119,1,"3","Bit","0x40","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE20.Port In4-I",1119,1,"3","Bit","0x80","-","État de l'entrée du module : Affectation du signal d'entrée"]
["Logiqu","LE20.Réin mémor-I",1119,1,"3","Bit","0x100","-","État de l'entrée du module : Signal de réinitialisation pour la mémorisation de l'état"]
["Modbus","Scada Cmd 1",1005,1,"3","Bit","0x1","-","Commande Scada "]
["Modbus","Scada Cmd 2",1005,1,"3","Bit","0x2","-","Commande Scada "]
["Modbus","Scada Cmd 3",1005,1,"3","Bit","0x4","-","Commande Scada "]
["Modbus","Scada Cmd 4",1005,1,"3","Bit","0x8","-","Commande Scada "]
["Modbus","Scada Cmd 5",1005,1,"3","Bit","0x10","-","Commande Scada "]
["Modbus","Scada Cmd 6",1005,1,"3","Bit","0x20","-","Commande Scada "]
["Modbus","Scada Cmd 7",1005,1,"3","Bit","0x40","-","Commande Scada "]
["Modbus","Scada Cmd 8",1005,1,"3","Bit","0x80","-","Commande Scada "]
["Modbus","Scada Cmd 9",1005,1,"3","Bit","0x100","-","Commande Scada "]
["Modbus","Scada Cmd 10",1005,1,"3","Bit","0x200","-","Commande Scada "]
["Modbus","Scada Cmd 11",1005,1,"3","Bit","0x400","-","Commande Scada "]
["Modbus","Scada Cmd 12",1005,1,"3","Bit","0x800","-","Commande Scada "]
["Modbus","Scada Cmd 13",1005,1,"3","Bit","0x1000","-","Commande Scada "]
["Modbus","Scada Cmd 14",1005,1,"3","Bit","0x2000","-","Commande Scada "]
["Modbus","Scada Cmd 15",1005,1,"3","Bit","0x4000","-","Commande Scada "]
["Modbus","Scada Cmd 16",1005,1,"3","Bit","0x8000","-","Commande Scada "]
["PF[1]","ExBlo1-I",73,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["PF[1]","ExBlo2-I",73,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["PF[1]","ExBlo TripCmd-I",73,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["PF[1]","actif",73,1,"3","Bit","0x8","-","Signal : actif"]
["PF[1]","ExBlo",73,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["PF[1]","Blo TripCmd",73,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["PF[1]","ExBlo TripCmd",73,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["PF[1]","Alarm",73,1,"3","Bit","0x80","-","Signal : Alarme de facteur de puissance"]
["PF[1]","Décl (*)",73,1,"3","Bit","0x100","-","Signal : Déclenchement sur facteur de puissance"]
["PF[1]","TripCmd (*)",73,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["PF[1]","Compensatr",73,1,"3","Bit","0x400","-","Signal : Signal de compensation"]
["PF[1]","Impossible",73,1,"3","Bit","0x800","-","Signal : Alarme de facteur de puissance impossible"]
["PF[2]","ExBlo1-I",74,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["PF[2]","ExBlo2-I",74,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["PF[2]","ExBlo TripCmd-I",74,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["PF[2]","actif",74,1,"3","Bit","0x8","-","Signal : actif"]
["PF[2]","ExBlo",74,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["PF[2]","Blo TripCmd",74,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["PF[2]","ExBlo TripCmd",74,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["PF[2]","Alarm",74,1,"3","Bit","0x80","-","Signal : Alarme de facteur de puissance"]
["PF[2]","Décl (*)",74,1,"3","Bit","0x100","-","Signal : Déclenchement sur facteur de puissance"]
["PF[2]","TripCmd (*)",74,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["PF[2]","Compensatr",74,1,"3","Bit","0x400","-","Signal : Signal de compensation"]
["PF[2]","Impossible",74,1,"3","Bit","0x800","-","Signal : Alarme de facteur de puissance impossible"]
["PQSCr","Cr Oflw Wp+",60,1,"3","Bit","0x1","-","Signal : Dépassement de capacité du compteur Wp+"]
["PQSCr","Cr Oflw Wp-",60,1,"3","Bit","0x2","-","Signal : Dépassement de capacité du compteur Wp-"]
["PQSCr","Cr Oflw Wq+",60,1,"3","Bit","0x4","-","Signal : Dépassement de capacité du compteur Wq+"]
["PQSCr","Cr Oflw Wq-",60,1,"3","Bit","0x8","-","Signal : Dépassement de capacité du compteur Wq-"]
["PQSCr","Cr Oflw Wp Net",60,1,"3","Bit","0x10","-","Signal : Dépassement de capacité du compteur Wp Net"]
["PQSCr","Cr Oflw Wq Net",60,1,"3","Bit","0x20","-","Signal : Dépassement de capacité du compteur Wq Net"]
["PQSCr","Cr Oflw Ws Net",60,1,"3","Bit","0x40","-","Signal : Dépassement de capacité du compteur Ws Net"]
["PQSCr","Cr OflwW Wp+",60,1,"3","Bit","0x80","-","Signal : Dépassement de capacité imminent du compteur Wp+ "]
["PQSCr","Cr OflwW Wp-",60,1,"3","Bit","0x100","-","Signal : Dépassement de capacité imminent du compteur Wp- "]
["PQSCr","Cr OflwW Wq+",60,1,"3","Bit","0x200","-","Signal : Dépassement de capacité imminent du compteur Wq+ "]
["PQSCr","Cr OflwW Wq-",60,1,"3","Bit","0x400","-","Signal : Dépassement de capacité imminent du compteur Wq- "]
["PQSCr","Cr OflwW Wp Net",60,1,"3","Bit","0x800","-","Signal : Dépassement de capacité imminent du compteur Wp Net "]
["PQSCr","Cr OflwW Wq Net",60,1,"3","Bit","0x1000","-","Signal : Dépassement de capacité imminent du compteur Wq Net "]
["PQSCr","Cr OflwW Ws Net",60,1,"3","Bit","0x2000","-","Signal : Dépassement de capacité imminent du compteur Ws Net"]
["PQS[1]","ExBlo1-I",67,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["PQS[1]","ExBlo2-I",67,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["PQS[1]","ExBlo TripCmd-I",67,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["PQS[1]","actif",67,1,"3","Bit","0x8","-","Signal : actif"]
["PQS[1]","ExBlo",67,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["PQS[1]","Blo TripCmd",67,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["PQS[1]","ExBlo TripCmd",67,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["PQS[1]","Alarm",67,1,"3","Bit","0x80","-","Signal : Alarme de protection de la puissance"]
["PQS[1]","Décl (*)",67,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la puissance "]
["PQS[1]","TripCmd (*)",67,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["PQS[2]","ExBlo1-I",68,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["PQS[2]","ExBlo2-I",68,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["PQS[2]","ExBlo TripCmd-I",68,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["PQS[2]","actif",68,1,"3","Bit","0x8","-","Signal : actif"]
["PQS[2]","ExBlo",68,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["PQS[2]","Blo TripCmd",68,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["PQS[2]","ExBlo TripCmd",68,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["PQS[2]","Alarm",68,1,"3","Bit","0x80","-","Signal : Alarme de protection de la puissance"]
["PQS[2]","Décl (*)",68,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la puissance "]
["PQS[2]","TripCmd (*)",68,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["PQS[3]","ExBlo1-I",69,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["PQS[3]","ExBlo2-I",69,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["PQS[3]","ExBlo TripCmd-I",69,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["PQS[3]","actif",69,1,"3","Bit","0x8","-","Signal : actif"]
["PQS[3]","ExBlo",69,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["PQS[3]","Blo TripCmd",69,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["PQS[3]","ExBlo TripCmd",69,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["PQS[3]","Alarm",69,1,"3","Bit","0x80","-","Signal : Alarme de protection de la puissance"]
["PQS[3]","Décl (*)",69,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la puissance "]
["PQS[3]","TripCmd (*)",69,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["PQS[4]","ExBlo1-I",70,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["PQS[4]","ExBlo2-I",70,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["PQS[4]","ExBlo TripCmd-I",70,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["PQS[4]","actif",70,1,"3","Bit","0x8","-","Signal : actif"]
["PQS[4]","ExBlo",70,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["PQS[4]","Blo TripCmd",70,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["PQS[4]","ExBlo TripCmd",70,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["PQS[4]","Alarm",70,1,"3","Bit","0x80","-","Signal : Alarme de protection de la puissance"]
["PQS[4]","Décl (*)",70,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la puissance "]
["PQS[4]","TripCmd (*)",70,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["PQS[5]","ExBlo1-I",71,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["PQS[5]","ExBlo2-I",71,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["PQS[5]","ExBlo TripCmd-I",71,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["PQS[5]","actif",71,1,"3","Bit","0x8","-","Signal : actif"]
["PQS[5]","ExBlo",71,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["PQS[5]","Blo TripCmd",71,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["PQS[5]","ExBlo TripCmd",71,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["PQS[5]","Alarm",71,1,"3","Bit","0x80","-","Signal : Alarme de protection de la puissance"]
["PQS[5]","Décl (*)",71,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la puissance "]
["PQS[5]","TripCmd (*)",71,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["PQS[6]","ExBlo1-I",72,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["PQS[6]","ExBlo2-I",72,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["PQS[6]","ExBlo TripCmd-I",72,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["PQS[6]","actif",72,1,"3","Bit","0x8","-","Signal : actif"]
["PQS[6]","ExBlo",72,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["PQS[6]","Blo TripCmd",72,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["PQS[6]","ExBlo TripCmd",72,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["PQS[6]","Alarm",72,1,"3","Bit","0x80","-","Signal : Alarme de protection de la puissance"]
["PQS[6]","Décl (*)",72,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la puissance "]
["PQS[6]","TripCmd (*)",72,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["PdP","ExBlo1-I",81,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["PdP","ExBlo2-I",81,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["PdP","actif",81,1,"3","Bit","0x4","-","Signal : actif"]
["PdP","ExBlo",81,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["PdP","Blo Pdp ",81,1,"3","Bit","0x10","-","Signal : La perte de potentiel bloque les autres fonctions."]
["PdP","Alarm",81,1,"3","Bit","0x20","-","Signal : Alarme de perte de potentiel"]
["PdP","Ex FF EVT",81,1,"3","Bit","0x1000","-","Signal:  Alarme de défaut de fusible de transformateurs de tension raccordés à la terre"]
["PdP","Ex FF VT",81,1,"3","Bit","0x2000","-","Signal: Ex FF VT"]
["PdP","Ex FF EVT-I",202,1,"3","Bit","0x1","-","État entrée module:  Alarme de défaut de fusible de transformateurs de tension raccordés à la terre"]
["PdP","Ex FF VT-I",202,1,"3","Bit","0x2","-","État entrée module:  Alarme de défaut de fusible de transformateurs de tension"]
["PdP","Blo décl.1-I",202,1,"3","Bit","0x4","-","État entrée module: Une alarme de cette fonction de protection bloque la détection de perte de potentiel."]
["PdP","Blo décl.2-I",202,1,"3","Bit","0x8","-","État entrée module: Une alarme de cette fonction de protection bloque la détection de perte de potentiel."]
["PdP","Blo décl.3-I",202,1,"3","Bit","0x10","-","État entrée module: Une alarme de cette fonction de protection bloque la détection de perte de potentiel."]
["PdP","Blo décl.4-I",202,1,"3","Bit","0x20","-","État entrée module: Une alarme de cette fonction de protection bloque la détection de perte de potentiel."]
["PdP","Blo décl.5-I",202,1,"3","Bit","0x40","-","État entrée module: Une alarme de cette fonction de protection bloque la détection de perte de potentiel."]
["Pr","ExBlo1-I",251,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["Pr","ExBlo2-I",251,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["Pr","ExBlo TripCmd-I",251,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["Pr","actif",251,1,"3","Bit","0x8","-","Signal : actif"]
["Pr","ExBlo",251,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["Pr","Blo TripCmd",251,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["Pr","ExBlo TripCmd",251,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["Pr","Alarm",251,1,"3","Bit","0x80","-","Signal : Alarme de protection de la puissance"]
["Pr","Décl (*)",251,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la puissance "]
["Pr","TripCmd (*)",251,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["Prot","ExBlo1-I",1,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["Prot","ExBlo2-I",1,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["Prot","actif",1,1,"3","Bit","0x4","-","Signal : actif"]
["Prot","ExBlo",1,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["Prot","Alar. L1",1,1,"3","Bit","0x10","-","Signal : Alarme générale L1"]
["Prot","Alar. L2",1,1,"3","Bit","0x20","-","Signal : Alarme générale L2"]
["Prot","Alar. L3",1,1,"3","Bit","0x40","-","Signal : Alarme générale L3"]
["Prot","Alar. G",1,1,"3","Bit","0x80","-","Signal : Alarme générale - Défaut à la terre"]
["Prot","Alarm",1,1,"3","Bit","0x100","-","Signal : Alarme générale"]
["Prot","Déc. L1 (*)",1,1,"3","Bit","0x200","-","Signal : Déclenchement général L1"]
["Prot","Déc. L2 (*)",1,1,"3","Bit","0x400","-","Signal : Déclenchement général L2"]
["Prot","Déc. L3 (*)",1,1,"3","Bit","0x800","-","Signal : Déclenchement général L3"]
["Prot","Déc. G (*)",1,1,"3","Bit","0x1000","-","Signal : Déclenchement général de défaut à la terre"]
["Prot","Décl (*)",1,1,"3","Bit","0x2000","-","Signal : Déclenchement général"]
["Prot","Blo TripCmd",2,1,"3","Bit","0x1","-","Signal : Commande de déclenchement bloquée"]
["Prot","ExBlo TripCmd-I",2,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["Prot","ExBlo TripCmd",2,1,"3","Bit","0x4","-","Signal : Blocage externe de la commande de déclenchement"]
["Prot","I dir fwd",2,1,"3","Bit","0x80","-","Signal : Défaut de courant de phase en sens direct"]
["Prot","I dir rev",2,1,"3","Bit","0x100","-","Signal : Défaut de courant de phase en sens inverse"]
["Prot","I dir n poss",2,1,"3","Bit","0x200","-","Signal : Défaut de phase - tension de référence absente"]
["Prot","N° de défaut",57,1,"3","Bit","0xffff","-","Nombre de défauts"]
["Prot","Nombre de défauts du réseau",58,1,"3","Bit","0xffff","-","Nombre de défauts du réseau : ce module comptabilise tous les défauts (par ex., les alarmes générales »Prot . Alarm«), à l'exception des défaillances qui surviennent lors d'un cycle d'exécution du module de réenclenchement automatique (signal »AR . Running«). (Remarque : le »Fault No.« compte chaque nouveau défaut indépendant des cycles de réenclenchement automatique). En d'autres termes, pour les appareils de protection sans module de réenclenchement automatique, ces deux compteurs sont équivalents."]
["Prot","IG calculé (dir arr)",200,1,"3","Bit","0x1","-","Signal : Défaut à  la terre (calculé) dans le sens inverse"]
["Prot","IG calc dir av",200,1,"3","Bit","0x2","-","Signal : Défaut à  la terre (calculé) dans le sens direct"]
["Prot","IG calc dir n poss",200,1,"3","Bit","0x4","-","Signal : Détection impossible de la direction d'un défaut à la terre (calculé)"]
["Prot","IG mesuré (dir arr)",200,1,"3","Bit","0x8","-","Signal : Défaut à  la terre (mesuré) dans le sens inverse"]
["Prot","IG mes dir av",200,1,"3","Bit","0x10","-","Signal : Défaut à  la terre (mesuré) dans le sens direct"]
["Prot","IG mes dir n poss",200,1,"3","Bit","0x20","-","Signal : Détection impossible de la direction d'un défaut à la terre (mesuré)"]
["Q->&V<","ExBlo1-I",157,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["Q->&V<","ExBlo2-I",157,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["Q->&V<","actif",157,1,"3","Bit","0x4","-","Signal : actif"]
["Q->&V<","ExBlo",157,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["Q->&V<","Déf fus. blo TT",157,1,"3","Bit","0x10","-","Signal : Bloqué par un fusible défectueux (VT)"]
["Q->&V<","Alarm",157,1,"3","Bit","0x20","-","Signal : Alarme de protection de tension insuffisante de la puissance réactive"]
["Q->&V<","Découplage PCC",157,1,"3","Bit","0x200","-","Signal : Découplage au point de couplage commun"]
["Q->&V<","Générat. distrib. de découp.",157,1,"3","Bit","0x400","-","Signal : Découplage du générateur/de la source d'énergie (locale)"]
["Qr","ExBlo1-I",252,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["Qr","ExBlo2-I",252,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["Qr","ExBlo TripCmd-I",252,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["Qr","actif",252,1,"3","Bit","0x8","-","Signal : actif"]
["Qr","ExBlo",252,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["Qr","Blo TripCmd",252,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["Qr","ExBlo TripCmd",252,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["Qr","Alarm",252,1,"3","Bit","0x80","-","Signal : Alarme de protection de la puissance"]
["Qr","Décl (*)",252,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la puissance "]
["Qr","TripCmd (*)",252,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["Recon[1]","ExBlo1-I",158,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["Recon[1]","ExBlo2-I",158,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["Recon[1]","actif",158,1,"3","Bit","0x4","-","Signal : actif"]
["Recon[1]","ExBlo",158,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["Recon[1]","Bloc. par superv. du circ. de mes.",158,1,"3","Bit","0x10","-","Signal: Module bloqué par la supervision du circuit de mesure"]
["Recon[1]","reconnecté-I",158,1,"3","Bit","0x20","-","Ce signal indique l'état  \"reconnecté\" (couplage réseau)."]
["Recon[1]","Débl ext V PCC Fc-I",158,1,"3","Bit","0x40","-","État d'entrée d'un module : Le signal de déblocage est créé par le point de couplage commun (PCC) (déblocage externe)"]
["Recon[1]","Déf fu ex TT PCC-I",158,1,"3","Bit","0x80","-","État entrée module: Blocage si le fusible d'un transformateur de tension s'est déclenché sur le point de couplage commun (PCC)."]
["Recon[1]","Débloc source énergie",158,1,"3","Bit","0x100","-","Signal : déblocage de la source d'énergie."]
["Recon[1]","Découplage1-I",158,1,"3","Bit","0x200","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[1]","Découplage2-I",158,1,"3","Bit","0x400","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[1]","Découplage3-I",158,1,"3","Bit","0x800","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[1]","Découplage4-I",158,1,"3","Bit","0x1000","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[1]","Découplage5-I",158,1,"3","Bit","0x2000","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[1]","Découplage6-I",158,1,"3","Bit","0x4000","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[2]","ExBlo1-I",159,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["Recon[2]","ExBlo2-I",159,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["Recon[2]","actif",159,1,"3","Bit","0x4","-","Signal : actif"]
["Recon[2]","ExBlo",159,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["Recon[2]","Bloc. par superv. du circ. de mes.",159,1,"3","Bit","0x10","-","Signal: Module bloqué par la supervision du circuit de mesure"]
["Recon[2]","reconnecté-I",159,1,"3","Bit","0x20","-","Ce signal indique l'état  \"reconnecté\" (couplage réseau)."]
["Recon[2]","Débl ext V PCC Fc-I",159,1,"3","Bit","0x40","-","État d'entrée d'un module : Le signal de déblocage est créé par le point de couplage commun (PCC) (déblocage externe)"]
["Recon[2]","Déf fu ex TT PCC-I",159,1,"3","Bit","0x80","-","État entrée module: Blocage si le fusible d'un transformateur de tension s'est déclenché sur le point de couplage commun (PCC)."]
["Recon[2]","Débloc source énergie",159,1,"3","Bit","0x100","-","Signal : déblocage de la source d'énergie."]
["Recon[2]","Découplage1-I",159,1,"3","Bit","0x200","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[2]","Découplage2-I",159,1,"3","Bit","0x400","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[2]","Découplage3-I",159,1,"3","Bit","0x800","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[2]","Découplage4-I",159,1,"3","Bit","0x1000","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[2]","Découplage5-I",159,1,"3","Bit","0x2000","-","Fonction de découplage qui bloque le réenclenchement."]
["Recon[2]","Découplage6-I",159,1,"3","Bit","0x4000","-","Fonction de découplage qui bloque le réenclenchement."]
["Registre d'état rapide","Device Type",5000,1,"3","Bit","0xffff","-","Device Type (Type de module) : code du type de module pour la mise en relation entre le nom du module et son code Modbus.\\n\\nWoodward:\\nMRI4 - 1000\\nMRU4 - 1001\\nMRA4 - 1002\\nMCA4 - 1003\\nMRDT4 - 1005\\nMCDTV4 - 1006\\nMCDGV4 - 1007\\nMRM4 - 1009\\nMRMV4 - 1010\\nMCDLV4 - 1011"]
["Registre d'état rapide","Version Comm",5001,1,"3","Bit","0xffff","-","Version de communication Modbus. Ce numéro de version change si une incompatibilité est présente entre différentes versions de Modbus."]
["Registre d'état rapide","Entr bin config1-I",5002,1,"3","Bit","0x1","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config2-I",5002,1,"3","Bit","0x2","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config3-I",5002,1,"3","Bit","0x4","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config4-I",5002,1,"3","Bit","0x8","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config5-I",5002,1,"3","Bit","0x10","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config6-I",5002,1,"3","Bit","0x20","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config7-I",5002,1,"3","Bit","0x40","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config8-I",5002,1,"3","Bit","0x80","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config9-I",5002,1,"3","Bit","0x100","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config10-I",5002,1,"3","Bit","0x200","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config11-I",5002,1,"3","Bit","0x400","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config12-I",5002,1,"3","Bit","0x800","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config13-I",5002,1,"3","Bit","0x1000","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config14-I",5002,1,"3","Bit","0x2000","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config15-I",5002,1,"3","Bit","0x4000","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config16-I",5002,1,"3","Bit","0x8000","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config17-I",5003,1,"3","Bit","0x1","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config18-I",5003,1,"3","Bit","0x2","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config19-I",5003,1,"3","Bit","0x4","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config20-I",5003,1,"3","Bit","0x8","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config21-I",5003,1,"3","Bit","0x10","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config22-I",5003,1,"3","Bit","0x20","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config23-I",5003,1,"3","Bit","0x40","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config24-I",5003,1,"3","Bit","0x80","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config25-I",5003,1,"3","Bit","0x100","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config26-I",5003,1,"3","Bit","0x200","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config27-I",5003,1,"3","Bit","0x400","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config28-I",5003,1,"3","Bit","0x800","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config29-I",5003,1,"3","Bit","0x1000","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config30-I",5003,1,"3","Bit","0x2000","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config31-I",5003,1,"3","Bit","0x4000","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Entr bin config32-I",5003,1,"3","Bit","0x8000","-","État entrée module: Entr bin config"]
["Registre d'état rapide","Cause du déclenchement (*)",5004,1,"3","Bit","0xffff","-","Cause initiale du déclenchement, présentée sous forme de valeur entière et correspond à l’entrée « Déclenchement » dans l’enregistrement des défauts, qui fait référence au nom du module de protection où le premier déclenchement s’est produit. Rechercher la définition de ces valeurs entières (c’est-à-dire, code de déclenchement de mappage-->nom du module) dans le tableau « Cause de déclenchement » fourni dans la documentation SCADA."]
["SG[1]","Aux OFF-I",177,1,"3","Bit","0x1","-","État d'entrée d'un module : Indicateur / signal de position du disjoncteur (52b)"]
["SG[1]","Aux ON-I",177,1,"3","Bit","0x2","-","État d'entrée d'un module : Indicateur / signal de position du disjoncteur (52a)"]
["SG[1]","Prêt-I",177,1,"3","Bit","0x4","-","État d'entrée d'un module : Disjoncteur prêt"]
["SG[1]","Sys-in-Sync-I",177,1,"3","Bit","0x8","-","État entrée module: Ce signal doit prendre la valeur 'vrai' pendant le temps de synchronisation. Sinon la commutation échoue."]
["SG[1]","Sécu OFF1-I",177,1,"3","Bit","0x10","-","État entrée module: Verrouillage de sécurité de la commande OFF "]
["SG[1]","Sécu OFF2-I",177,1,"3","Bit","0x20","-","État entrée module: Verrouillage de sécurité de la commande OFF "]
["SG[1]","Sécu OFF3-I",177,1,"3","Bit","0x40","-","État entrée module: Verrouillage de sécurité de la commande OFF "]
["SG[1]","Sécu ON1-I",177,1,"3","Bit","0x80","-","État entrée module: Verrouillage de sécurité de la commande ON "]
["SG[1]","Sécu ON2-I",177,1,"3","Bit","0x100","-","État entrée module: Verrouillage de sécurité de la commande ON "]
["SG[1]","Sécu ON3-I",177,1,"3","Bit","0x200","-","État entrée module: Verrouillage de sécurité de la commande ON "]
["SG[1]","SCmd OFF-I",177,1,"3","Bit","0x800","-","État entrée module: Commande de désactivation (OFF) ; ex. état de la logique ou de l'état de l'entrée numérique"]
["SG[1]","SCmd ON-I",177,1,"3","Bit","0x1000","-","État entrée module: Commande d'activation (ON) ; ex. état de la logique ou de l'état de l'entrée numérique"]
["SG[1]","TripCmd (*)",177,1,"3","Bit","0x2000","-","Signal : Commande de déclenchement"]
["SG[1]","Cmd OFF",177,1,"3","Bit","0x4000","-","Signal: Commande OFF envoyée à l'appareillage de connexion. En fonction de la configuration, le signal peut comprendre la commande OFF du module de protection."]
["SG[1]","Cmd OFF manuel",177,1,"3","Bit","0x8000","-","Signal: Cmd OFF manuel"]
["SG[1]","Cmd ON",178,1,"3","Bit","0x1","-","Signal: Commande ON envoyée à l'appareillage de connexion. En fonction de la configuration, le signal peut comprendre la commande ON du module de protection."]
["SG[1]","Cmd ON manuel",178,1,"3","Bit","0x2","-","Signal: Cmd ON manuel"]
["SG[1]","Dem sync ON",178,1,"3","Bit","0x4","-","Signal: Demande de commande ON synchrone"]
["SG[1]","SGwear SG lent",178,1,"3","Bit","0x8","-","Signal: Alarme ; le disjoncteur (contacteur de coupure de la charge) est plus lent"]
["SG[1]","Réi SGwear Sl SG",178,1,"3","Bit","0x10","-","Signal: Réinitialisation de l'alarme d'appareillage de connexion lent"]
["SG[1]","CES perturbé",178,1,"3","Bit","0x40","-","Signal: Surveillance d'exécution des commandes : échec de commande de commutation. Appareillage de connexion en position perturbée."]
["SG[1]","CES Fiel Séc",178,1,"3","Bit","0x80","-","Signal: Surveillance d'exécution des commandes : Commande de commutation non exécutée à cause d'un verrouillage de sécurité du champ."]
["SG[1]","CES ON d OFF",178,1,"3","Bit","0x400","-","Signal: Surveillance d'exécution des commandes : Commande ON pendant une commande OFF en attente."]
["SG[1]","CES SwitchgDir",178,1,"3","Bit","0x800","-","Signal: Surveillance d'exécution des commandes par rapport au contrôle de la direction de commutation : ce signal prend la valeur 'vrai' si une commande de commutation est émise même si l'appareillage de connexion est déjà dans la position demandée. Exemple :  un appareillage de connexion qui est déjà en position OFF doit être à nouveau commuté en position OFF.  Cela s'applique également aux commandes de fermeture."]
["SG[1]","CES SG pas prêt",178,1,"3","Bit","0x1000","-","Signal: Surveillance d'exécution des commandes : l'appareillage de connexion n'est pas prêt"]
["SG[1]","CES SyncTimeout",178,1,"3","Bit","0x2000","-","Signal: Surveillance d'exécution des commandes : commande de commutation non exécutée. Pas de signal de synchronisation pendant l'exécution de t-sync."]
["SG[1]","CES réussi",178,1,"3","Bit","0x4000","-","Signal: Surveillance d'exécution des commandes : commande d'exécution réussie."]
["SG[1]","Prot ON",178,1,"3","Bit","0x8000","-","Signal: Commande ON émise par le module de protection"]
["SG[1]","Pos perturb",179,1,"3","Bit","0x1","-","Signal : Disjoncteur perturbé - Position du disjoncteur indéterminée. Les indicateurs de position sont contradictoires. A l'expiration de la temporisation de surveillance, ce signal prend la valeur 'vrai'."]
["SG[1]","t-paus",179,1,"3","Bit","0x2","-","Signal: Temps mort "]
["SG[1]","Pos indéterm",179,1,"3","Bit","0x4","-","Signal : Le disjoncteur est en position indéterminée"]
["SG[1]","Pos OFF",179,1,"3","Bit","0x8","-","Signal : Le disjoncteur est en position OFF"]
["SG[1]","Pos ON",179,1,"3","Bit","0x10","-","Signal : Le disjoncteur est en position ON"]
["SG[1]","Prêt",179,1,"3","Bit","0x20","-","Signal : Le disjoncteur est prêt à fonctionner."]
["SG[1]","Pos pas ON",179,1,"3","Bit","0x40","-","Signal: Pos pas ON"]
["SG[1]","SI SingleContactInd",179,1,"3","Bit","0x80","-","Signal: La position de l'appareillage de connexion est détectée uniquement par un contact auxiliaire (pôle). Il n'est donc pas possible de détecter les positions indéterminées et perturbées."]
["SG[1]","Position manip ind",179,1,"3","Bit","0x100","-","Signal: Indicateurs de position factices"]
["SG[1]","OFF incl TripCmd",179,1,"3","Bit","0x200","-","Signal: La commande OFF comprend la commande OFF émise par le module de protection."]
["SG[1]","ON incl Prot ON",179,1,"3","Bit","0x400","-","Signal: La commande ON comprend la commande ON émise par le module de protection."]
["SG[1]","CES déf TripCmd",179,1,"3","Bit","0x800","-","Signal: Surveillance d'exécution des commandes : l'exécution des commandes a échoué parce qu'une commande de déclenchement est en attente."]
["SG[1]","Sécu OFF",179,1,"3","Bit","0x1000","-","Signal: Une ou plusieurs entrées IL_Off sont actives."]
["SG[1]","Sécu ON",179,1,"3","Bit","0x2000","-","Signal: Une ou plusieurs entrées IL_On sont actives."]
["SG[1]","Déc Isum Intr",195,1,"3","Bit","0x10","-","Signal : Dépassement de la somme maximale admissible des courants de coupure (déclenchement) dans au moins une phase."]
["SG[1]","Déc Isum Intr:  IL1",195,1,"3","Bit","0x20","-","Signal : Dépassement de la somme maximale admissible des courants de coupure (déclenchement):  IL1"]
["SG[1]","Déc Isum Intr:  IL2",195,1,"3","Bit","0x40","-","Signal : Dépassement de la somme maximale admissible des courants de coupure (déclenchement):  IL2"]
["SG[1]","Déc Isum Intr:  IL3",195,1,"3","Bit","0x80","-","Signal : Dépassement de la somme maximale admissible des courants de coupure (déclenchement):  IL3"]
["SG[1]","Alarm opérations",195,1,"3","Bit","0x100","-","Signal : trop d’opérations. (Le compteur d’opérations »Compt. cmdes déclench.« a dépassé la limite définie pour »Alarme opérations«.)"]
["SG[1]","Alarm WearLevel",195,1,"3","Bit","0x200","-","Signal: Seuil de l'alarme "]
["SG[1]","Débloc WearLevel",195,1,"3","Bit","0x400","-","Signal: Seuil du verrouillage"]
["SG[1]","Isum Intr ph Alm",195,1,"3","Bit","0x800","-","Signal: Alarme : la somme par heure (limite) de courant de coupure est dépassée."]
["SG[1]","Supprim-I",256,1,"3","Bit","0x1","-","État entrée module: Le disjoncteur débrochable est enlevé"]
["SG[1]","CES SG supprimé",256,1,"3","Bit","0x2","-","Signal: Surveillance d'exécution des commandes : Échec de commande de commutation, appareillage de connexion supprimé."]
["SG[1]","Supprim",256,1,"3","Bit","0x4","-","Signal: Le disjoncteur débrochable est enlevé"]
["SOTF","ExBlo1-I",65,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["SOTF","ExBlo2-I",65,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe"]
["SOTF","SOTF ext-I",65,1,"3","Bit","0x4","-","État d'entrée d'un module : Alarme de commutation sur défaut externe "]
["SOTF","Ex rev Interl-I",65,1,"3","Bit","0x8","-","État d'entrée d'un module : Verrouillage externe"]
["SOTF","actif",65,1,"3","Bit","0x10","-","Signal : actif"]
["SOTF","ExBlo",65,1,"3","Bit","0x20","-","Signal : Blocage externe"]
["SOTF","Ex rev Interl",65,1,"3","Bit","0x40","-","Signal : Verrouillage externe"]
["SOTF","Blo RA",65,1,"3","Bit","0x400","-","Signal : Bloqué par le réenclenchement automatique"]
["SOTF","activé",65,1,"3","Bit","0x800","-","Signal : Commutation sur défaut activée Ce signal est utilisable pour modifier les paramètres de protection contre les surintensités."]
["SOTF","I<",65,1,"3","Bit","0x2000","-","Signal : Pas de courant de charge."]
["SSV","Erreur système",273,1,"3","Bit","0x1","-","Signal: Défaillance du module"]
["SSV","Nouvelle erreur (*)",273,1,"3","Bit","0x8","-","Signal: Un nouveau message d’erreur a été émis."]
["SSV","Nouvel avertissement (*)",273,1,"3","Bit","0x10","-","Signal: Un nouveau message d’avertissement a été émis."]
["SSV","actif",273,1,"3","Bit","0x20","-","Signal : actif"]
["Sgen","ExBlo1-I",1012,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["Sgen","Ex ForcePost-I",1012,1,"3","Bit","0x2","-","État entrée module:Forcer l'état postérieur. Abandonner la simulation."]
["Sgen","Exéc.",1012,1,"3","Bit","0x10","-","Signal ; la simulation de la valeur mesurée est en cours d'exécution"]
["Sgen","État",1012,1,"3","Bit","0xe0","-","Signal : États de génération des signaux : 0=Off, 1=Pré défaut, 2=Défaut, 3=Post défaut, 4=InitReset"]
["Sgen","Démar simul ex-I",1012,1,"3","Bit","0x100","-","État entrée module:Démarrage externe de la simulation de défauts (en utilisant les paramètres de test)"]
["Sgen","ExBlo2-I",1012,1,"3","Bit","0x200","-","État d'entrée d'un module : Blocage externe2"]
["Sgen","Démarrage manuel",1012,1,"3","Bit","0x400","-","La simulation de défauts a été démarrée manuellement."]
["Sgen","Arrêt manuel",1012,1,"3","Bit","0x800","-","La simulation de défauts a été arrêtée manuellement."]
["Sgen","Démarrée",1012,1,"3","Bit","0x1000","-","La simulation de défauts a été démarrée"]
["Sgen","Arrêtée",1012,1,"3","Bit","0x2000","-","La simulation de défauts a été arrêtée"]
["Sync","actif",175,1,"3","Bit","0x1","-","Signal : actif"]
["Sync","ExBlo1-I",175,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe1"]
["Sync","ExBlo2-I",175,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe2"]
["Sync","ExBlo",175,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["Sync","Dériv-I",175,1,"3","Bit","0x10","-","État entrée module: Le contrôle de la synchronisation est ignoré si l'état du signal affecté (entrée logique) prend la valeur 'vrai'."]
["Sync","CBCloseInitiate-I",175,1,"3","Bit","0x20","-","État entrée module: Lancement de la fermeture du disjoncteur avec contrôle du synchronisme provenant de n'importe quelle source de commande (ex. pupitre opérateur / système SCADA). Si l'état du signal affecté prend la valeur 'vrai', la fermeture du disjoncteur se produit (origine du déclenchement)."]
["Sync","AngleDiffTooHigh",175,1,"3","Bit","0x40","-","Signal: Différence d'angle de phase trop élevée entre le bus et la ligne."]
["Sync","Sys-in-Sync",175,1,"3","Bit","0x80","-","Signal: Les tensions du bus et de la ligne sont en synchronisme d'après les conditions de synchronisme du réseau."]
["Sync","LiveBus",175,1,"3","Bit","0x100","-","Signal: Marqueur de bus sous tension : 1=bus sous tension, 0=tension inférieure au seuil de tension du bus"]
["Sync","LiveLine",175,1,"3","Bit","0x200","-","Signal: Marqueur de ligne sous tension : 1=ligne sous tension, 0=tension inférieure au seuil de tension de la ligne"]
["Sync","SlipTooHigh",175,1,"3","Bit","0x400","-","Signal: Différence de fréquence (glissement de fréquence) trop élevée entre les tensions de bus et de ligne."]
["Sync","SyncOverridden",175,1,"3","Bit","0x800","-","Signal:Le contrôle du synchronisme est ignoré parce qu'une des conditions de priorité du synchronisme (DB/DL ou ExtBypass) est remplie."]
["Sync","Prêt à fermer",175,1,"3","Bit","0x1000","-","Signal: Prêt à fermer"]
["Sync","SynchronFailed",175,1,"3","Bit","0x2000","-","Signal: Ce signal indique l'échec de la synchronisation. Il est réglé sur 5 s lorsque le disjoncteur est toujours ouvert lorsque la temporisation Synchron/Fonctionnement a expiré."]
["Sync","SynchronRunTiming",175,1,"3","Bit","0x4000","-","Signal: Temporisation Synchron/Fonctionnement en cours (cette temporisation commence au lancement de la fermeture et s'arrête si le disjoncteur est fermé. La temporisation écoulée signifie que la synchronisation a échoué)."]
["Sync","VDiffTooHigh",175,1,"3","Bit","0x8000","-","Signal: Différence de tension trop élevée entre le bus et la ligne."]
["Sys","Configuration du verrouillage-I",154,1,"3","Bit","0x40","-","État entrée module: Aucun paramètre n'est modifiable tant que cette entrée a la valeur 'vrai'. Le paramétrage est verrouillé."]
["Sys","SNTP actif",154,1,"3","Bit","0x80","-","Signal: S'il n'y a pas de signal SNTP valide pendant 120 s, le protocole SNTP est considéré inactif."]
["Sys","Conf dériv verr",154,1,"3","Bit","0x100","-","Signal: Déverrouillage bref "]
["SysA","ExBlo-I",173,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe"]
["SysA","ExBlo",173,1,"3","Bit","0x2","-","Signal : Blocage externe"]
["SysA","Alm dmd moy courant",173,1,"3","Bit","0x4","-","Signal: Alarme de dépassement de la demande moyenne de courant"]
["SysA","actif",173,1,"3","Bit","0x8","-","Signal : actif"]
["SysA","Alarm I THD",173,1,"3","Bit","0x10","-","Signal: Alarme de courant de distorsion harmonique totale "]
["SysA","Alarm puiss VA max",173,1,"3","Bit","0x20","-","Signal: Alarme de dépassement de la puissance apparente autorisée"]
["SysA","Alarm demand VA moy",173,1,"3","Bit","0x40","-","Signal: Alarme de dépassement de la puissance apparente moyenne"]
["SysA","Alarm puiss Var max",173,1,"3","Bit","0x80","-","Signal: Alarme de dépassement de la puissance réactive autorisée"]
["SysA","Alarm demand Var moy",173,1,"3","Bit","0x100","-","Signal: Alarme de dépassement de la puissance réactive moyenne"]
["SysA","Alarm V THD",173,1,"3","Bit","0x200","-","Signal: Alarme de tension de distorsion harmonique totale "]
["SysA","Alarm puiss Watt max",173,1,"3","Bit","0x400","-","Signal: Alarme de dépassement de la puissance active autorisée"]
["SysA","Alarm demand Watt moy",173,1,"3","Bit","0x800","-","Signal: Alarme de dépassement de la puissance active moyenne"]
["SysA","Dmd moy courant décl (*)",173,1,"3","Bit","0x1000","-","Signal: Déclenchement sur dépassement de la demande moyenne de courant"]
["SysA","Décl I THD (*)",173,1,"3","Bit","0x2000","-","Signal: Déclenchement sur courant de distorsion harmonique totale "]
["SysA","Décl demand VA moy (*)",173,1,"3","Bit","0x4000","-","Signal: Déclenchement sur dépassement de la puissance apparente moyenne"]
["SysA","Décl puiss VA max (*)",173,1,"3","Bit","0x8000","-","Signal: Déclenchement sur dépassement de la puissance apparente maximale autorisée"]
["SysA","Décl demand VAr moy (*)",174,1,"3","Bit","0x1","-","Signal: Déclenchement sur dépassement de la puissance réactive moyenne"]
["SysA","Décl puiss Var max (*)",174,1,"3","Bit","0x2","-","Signal: Déclenchement sur dépassement de la puissance réactive maximale autorisée"]
["SysA","Décl V THD (*)",174,1,"3","Bit","0x4","-","Signal: Déclenchement sur tension de distorsion harmonique totale "]
["SysA","Décl demand Watt moy (*)",174,1,"3","Bit","0x8","-","Signal: Déclenchement sur dépassement de la puissance active moyenne"]
["SysA","Décl puiss Watt max (*)",174,1,"3","Bit","0x10","-","Signal: Déclenchement sur dépassement de la puissance active maximale autorisée"]
["TCS","ExBlo1-I",150,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["TCS","ExBlo2-I",150,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["TCS","actif",150,1,"3","Bit","0x4","-","Signal : actif"]
["TCS","ExBlo",150,1,"3","Bit","0x8","-","Signal : Blocage externe"]
["TCS","Alarm",150,1,"3","Bit","0x10","-","Signal : Alarme de déclenchement de surveillance de circuit "]
["TCS","Impossible",150,1,"3","Bit","0x20","-","Impossible car aucun indicateur d'état n'est affecté au disjoncteur."]
["TCS","Aux ON-I",150,1,"3","Bit","0x100","-","État d'entrée d'un module : Indicateur / signal de position du disjoncteur (52a)"]
["TCS","Aux OFF-I",150,1,"3","Bit","0x200","-","État d'entrée d'un module : Indicateur / signal de position du disjoncteur (52b)"]
["ThR","ExBlo1-I",19,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["ThR","ExBlo2-I",19,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["ThR","ExBlo TripCmd-I",19,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["ThR","actif",19,1,"3","Bit","0x8","-","Signal : actif"]
["ThR","ExBlo",19,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["ThR","Blo TripCmd",19,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["ThR","ExBlo TripCmd",19,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["ThR","Alarm",19,1,"3","Bit","0x80","-","Signal : Alarme de surcharge thermique"]
["ThR","Décl (*)",19,1,"3","Bit","0x100","-","Signal : Décl"]
["ThR","TripCmd (*)",19,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["TimeSync","synchronized",54,1,"3","Bit","0x1","-","L'horloge est synchronisée."]
["UFLS","ExBlo1-I",272,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["UFLS","ExBlo2-I",272,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["UFLS","Ex Pdir-I",272,1,"3","Bit","0x4","-","Ignore (bloc) l'évaluation de la direction du flux de puissance. Il en résulte une fréquence classique basée sur la fonction de délestage de charge. Lorsque cette fonction est définie et active, la fonctionalité du module se transforme en délestage de charge conventionnel, uniquement basé sur la fréquence."]
["UFLS","actif",272,1,"3","Bit","0x8","-","Signal : actif"]
["UFLS","ExBlo",272,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["UFLS","Déf fus. blo TT",272,1,"3","Bit","0x20","-","Signal : Bloqué par un fusible défectueux (VT)"]
["UFLS","Décl",272,1,"3","Bit","0x40","-","Signal: Signal : Décl"]
["UFLS","Alarme",272,1,"3","Bit","0x80","-","Signal : Alarme P ->&f<"]
["U[1]","ExBlo1-I",24,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["U[1]","ExBlo2-I",24,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["U[1]","ExBlo TripCmd-I",24,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["U[1]","actif",24,1,"3","Bit","0x8","-","Signal : actif"]
["U[1]","ExBlo",24,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["U[1]","Blo TripCmd",24,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["U[1]","ExBlo TripCmd",24,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["U[1]","Alar. L1",25,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["U[1]","Alar. L2",25,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["U[1]","Alar. L3",25,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["U[1]","Alarm",25,1,"3","Bit","0x8","-","Signal : Alarme de l'étage de tension"]
["U[1]","Déc. L1 (*)",25,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["U[1]","Déc. L2 (*)",25,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["U[1]","Déc. L3 (*)",25,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["U[1]","Décl (*)",25,1,"3","Bit","0x80","-","Signal : Décl"]
["U[1]","TripCmd (*)",25,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["U[1]","Contrôle Imin actif",25,1,"3","Bit","0x200","-","Signale que le contrôle de Imin (courant minimum) est actif et qu'il ne bloque pas (à l'instant T) le déclenchement du module Détection de sous-tension."]
["U[2]","ExBlo1-I",26,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["U[2]","ExBlo2-I",26,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["U[2]","ExBlo TripCmd-I",26,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["U[2]","actif",26,1,"3","Bit","0x8","-","Signal : actif"]
["U[2]","ExBlo",26,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["U[2]","Blo TripCmd",26,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["U[2]","ExBlo TripCmd",26,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["U[2]","Alar. L1",27,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["U[2]","Alar. L2",27,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["U[2]","Alar. L3",27,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["U[2]","Alarm",27,1,"3","Bit","0x8","-","Signal : Alarme de l'étage de tension"]
["U[2]","Déc. L1 (*)",27,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["U[2]","Déc. L2 (*)",27,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["U[2]","Déc. L3 (*)",27,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["U[2]","Décl (*)",27,1,"3","Bit","0x80","-","Signal : Décl"]
["U[2]","TripCmd (*)",27,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["U[2]","Contrôle Imin actif",27,1,"3","Bit","0x200","-","Signale que le contrôle de Imin (courant minimum) est actif et qu'il ne bloque pas (à l'instant T) le déclenchement du module Détection de sous-tension."]
["U[3]","ExBlo1-I",28,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["U[3]","ExBlo2-I",28,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["U[3]","ExBlo TripCmd-I",28,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["U[3]","actif",28,1,"3","Bit","0x8","-","Signal : actif"]
["U[3]","ExBlo",28,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["U[3]","Blo TripCmd",28,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["U[3]","ExBlo TripCmd",28,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["U[3]","Alar. L1",29,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["U[3]","Alar. L2",29,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["U[3]","Alar. L3",29,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["U[3]","Alarm",29,1,"3","Bit","0x8","-","Signal : Alarme de l'étage de tension"]
["U[3]","Déc. L1 (*)",29,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["U[3]","Déc. L2 (*)",29,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["U[3]","Déc. L3 (*)",29,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["U[3]","Décl (*)",29,1,"3","Bit","0x80","-","Signal : Décl"]
["U[3]","TripCmd (*)",29,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["U[3]","Contrôle Imin actif",29,1,"3","Bit","0x200","-","Signale que le contrôle de Imin (courant minimum) est actif et qu'il ne bloque pas (à l'instant T) le déclenchement du module Détection de sous-tension."]
["U[4]","ExBlo1-I",30,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["U[4]","ExBlo2-I",30,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["U[4]","ExBlo TripCmd-I",30,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["U[4]","actif",30,1,"3","Bit","0x8","-","Signal : actif"]
["U[4]","ExBlo",30,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["U[4]","Blo TripCmd",30,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["U[4]","ExBlo TripCmd",30,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["U[4]","Alar. L1",31,1,"3","Bit","0x1","-","Signal : Alarme L1"]
["U[4]","Alar. L2",31,1,"3","Bit","0x2","-","Signal : Alarme L2"]
["U[4]","Alar. L3",31,1,"3","Bit","0x4","-","Signal : Alarme L3"]
["U[4]","Alarm",31,1,"3","Bit","0x8","-","Signal : Alarme de l'étage de tension"]
["U[4]","Déc. L1 (*)",31,1,"3","Bit","0x10","-","Signal : Déclenchement général phase L1"]
["U[4]","Déc. L2 (*)",31,1,"3","Bit","0x20","-","Signal : Déclenchement général phase L2"]
["U[4]","Déc. L3 (*)",31,1,"3","Bit","0x40","-","Signal : Déclenchement général phase L3"]
["U[4]","Décl (*)",31,1,"3","Bit","0x80","-","Signal : Décl"]
["U[4]","TripCmd (*)",31,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["U[4]","Contrôle Imin actif",31,1,"3","Bit","0x200","-","Signale que le contrôle de Imin (courant minimum) est actif et qu'il ne bloque pas (à l'instant T) le déclenchement du module Détection de sous-tension."]
["U[5]","ExBlo1-I",92,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["U[5]","ExBlo2-I",92,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["U[5]","ExBlo TripCmd-I",92,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["U[5]","actif",92,1,"3","Bit","0x8","-","Signal : actif"]
["U[5]","ExBlo",92,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["U[5]","Blo TripCmd",92,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["U[5]","ExBlo TripCmd",92,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["U[5]","Alarm",92,1,"3","Bit","0x80","-","Signal : Alarme de l'étage de tension"]
["U[5]","Alar. L1",92,1,"3","Bit","0x100","-","Signal : Alarme L1"]
["U[5]","Alar. L2",92,1,"3","Bit","0x200","-","Signal : Alarme L2"]
["U[5]","Alar. L3",92,1,"3","Bit","0x400","-","Signal : Alarme L3"]
["U[5]","Décl (*)",92,1,"3","Bit","0x800","-","Signal : Décl"]
["U[5]","Déc. L1 (*)",92,1,"3","Bit","0x1000","-","Signal : Déclenchement général phase L1"]
["U[5]","Déc. L2 (*)",92,1,"3","Bit","0x2000","-","Signal : Déclenchement général phase L2"]
["U[5]","Déc. L3 (*)",92,1,"3","Bit","0x4000","-","Signal : Déclenchement général phase L3"]
["U[5]","TripCmd (*)",92,1,"3","Bit","0x8000","-","Signal : Commande de déclenchement"]
["U[5]","Contrôle Imin actif",94,1,"3","Bit","0x1","-","Signale que le contrôle de Imin (courant minimum) est actif et qu'il ne bloque pas (à l'instant T) le déclenchement du module Détection de sous-tension."]
["U[6]","ExBlo1-I",93,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["U[6]","ExBlo2-I",93,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["U[6]","ExBlo TripCmd-I",93,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["U[6]","actif",93,1,"3","Bit","0x8","-","Signal : actif"]
["U[6]","ExBlo",93,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["U[6]","Blo TripCmd",93,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["U[6]","ExBlo TripCmd",93,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["U[6]","Alarm",93,1,"3","Bit","0x80","-","Signal : Alarme de l'étage de tension"]
["U[6]","Alar. L1",93,1,"3","Bit","0x100","-","Signal : Alarme L1"]
["U[6]","Alar. L2",93,1,"3","Bit","0x200","-","Signal : Alarme L2"]
["U[6]","Alar. L3",93,1,"3","Bit","0x400","-","Signal : Alarme L3"]
["U[6]","Décl (*)",93,1,"3","Bit","0x800","-","Signal : Décl"]
["U[6]","Déc. L1 (*)",93,1,"3","Bit","0x1000","-","Signal : Déclenchement général phase L1"]
["U[6]","Déc. L2 (*)",93,1,"3","Bit","0x2000","-","Signal : Déclenchement général phase L2"]
["U[6]","Déc. L3 (*)",93,1,"3","Bit","0x4000","-","Signal : Déclenchement général phase L3"]
["U[6]","TripCmd (*)",93,1,"3","Bit","0x8000","-","Signal : Commande de déclenchement"]
["U[6]","Contrôle Imin actif",95,1,"3","Bit","0x1","-","Signale que le contrôle de Imin (courant minimum) est actif et qu'il ne bloque pas (à l'instant T) le déclenchement du module Détection de sous-tension."]
["V 012[1]","ExBlo1-I",100,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["V 012[1]","ExBlo2-I",100,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["V 012[1]","ExBlo TripCmd-I",100,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["V 012[1]","actif",100,1,"3","Bit","0x8","-","Signal : actif"]
["V 012[1]","ExBlo",100,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["V 012[1]","Blo TripCmd",100,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["V 012[1]","ExBlo TripCmd",100,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["V 012[1]","Alarm",100,1,"3","Bit","0x80","-","Signal : Alarme de tension asymétrique"]
["V 012[1]","Décl (*)",100,1,"3","Bit","0x100","-","Signal : Décl"]
["V 012[1]","TripCmd (*)",100,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["V 012[2]","ExBlo1-I",101,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["V 012[2]","ExBlo2-I",101,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["V 012[2]","ExBlo TripCmd-I",101,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["V 012[2]","actif",101,1,"3","Bit","0x8","-","Signal : actif"]
["V 012[2]","ExBlo",101,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["V 012[2]","Blo TripCmd",101,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["V 012[2]","ExBlo TripCmd",101,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["V 012[2]","Alarm",101,1,"3","Bit","0x80","-","Signal : Alarme de tension asymétrique"]
["V 012[2]","Décl (*)",101,1,"3","Bit","0x100","-","Signal : Décl"]
["V 012[2]","TripCmd (*)",101,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["V 012[3]","ExBlo1-I",102,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["V 012[3]","ExBlo2-I",102,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["V 012[3]","ExBlo TripCmd-I",102,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["V 012[3]","actif",102,1,"3","Bit","0x8","-","Signal : actif"]
["V 012[3]","ExBlo",102,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["V 012[3]","Blo TripCmd",102,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["V 012[3]","ExBlo TripCmd",102,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["V 012[3]","Alarm",102,1,"3","Bit","0x80","-","Signal : Alarme de tension asymétrique"]
["V 012[3]","Décl (*)",102,1,"3","Bit","0x100","-","Signal : Décl"]
["V 012[3]","TripCmd (*)",102,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["V 012[4]","ExBlo1-I",103,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["V 012[4]","ExBlo2-I",103,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["V 012[4]","ExBlo TripCmd-I",103,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["V 012[4]","actif",103,1,"3","Bit","0x8","-","Signal : actif"]
["V 012[4]","ExBlo",103,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["V 012[4]","Blo TripCmd",103,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["V 012[4]","ExBlo TripCmd",103,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["V 012[4]","Alarm",103,1,"3","Bit","0x80","-","Signal : Alarme de tension asymétrique"]
["V 012[4]","Décl (*)",103,1,"3","Bit","0x100","-","Signal : Décl"]
["V 012[4]","TripCmd (*)",103,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["V 012[5]","ExBlo1-I",104,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["V 012[5]","ExBlo2-I",104,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["V 012[5]","ExBlo TripCmd-I",104,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["V 012[5]","actif",104,1,"3","Bit","0x8","-","Signal : actif"]
["V 012[5]","ExBlo",104,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["V 012[5]","Blo TripCmd",104,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["V 012[5]","ExBlo TripCmd",104,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["V 012[5]","Alarm",104,1,"3","Bit","0x80","-","Signal : Alarme de tension asymétrique"]
["V 012[5]","Décl (*)",104,1,"3","Bit","0x100","-","Signal : Décl"]
["V 012[5]","TripCmd (*)",104,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["V 012[6]","ExBlo1-I",105,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["V 012[6]","ExBlo2-I",105,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["V 012[6]","ExBlo TripCmd-I",105,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["V 012[6]","actif",105,1,"3","Bit","0x8","-","Signal : actif"]
["V 012[6]","ExBlo",105,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["V 012[6]","Blo TripCmd",105,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["V 012[6]","ExBlo TripCmd",105,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["V 012[6]","Alarm",105,1,"3","Bit","0x80","-","Signal : Alarme de tension asymétrique"]
["V 012[6]","Décl (*)",105,1,"3","Bit","0x100","-","Signal : Décl"]
["V 012[6]","TripCmd (*)",105,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["VG[1]","ExBlo1-I",32,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["VG[1]","ExBlo2-I",32,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["VG[1]","ExBlo TripCmd-I",32,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["VG[1]","actif",32,1,"3","Bit","0x8","-","Signal : actif"]
["VG[1]","ExBlo",32,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["VG[1]","Blo TripCmd",32,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["VG[1]","ExBlo TripCmd",32,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["VG[1]","Alarm",32,1,"3","Bit","0x80","-","Signal : Alarme de l'étage de surveillance de la tension résiduelle"]
["VG[1]","Décl (*)",32,1,"3","Bit","0x100","-","Signal : Décl"]
["VG[1]","TripCmd (*)",32,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["VG[2]","ExBlo1-I",33,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["VG[2]","ExBlo2-I",33,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["VG[2]","ExBlo TripCmd-I",33,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["VG[2]","actif",33,1,"3","Bit","0x8","-","Signal : actif"]
["VG[2]","ExBlo",33,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["VG[2]","Blo TripCmd",33,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["VG[2]","ExBlo TripCmd",33,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["VG[2]","Alarm",33,1,"3","Bit","0x80","-","Signal : Alarme de l'étage de surveillance de la tension résiduelle"]
["VG[2]","Décl (*)",33,1,"3","Bit","0x100","-","Signal : Décl"]
["VG[2]","TripCmd (*)",33,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["delta phi","ExBlo1-I",249,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["delta phi","ExBlo2-I",249,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["delta phi","ExBlo TripCmd-I",249,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["delta phi","actif",249,1,"3","Bit","0x8","-","Signal : actif"]
["delta phi","ExBlo",249,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["delta phi","Blo TripCmd",249,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["delta phi","ExBlo TripCmd",249,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["delta phi","Alarm",249,1,"3","Bit","0x80","-","Signal : Alarme de protection de la fréquence (signal collectif)"]
["delta phi","Décl (*)",249,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la fréquence (signal collectif)"]
["delta phi","TripCmd (*)",249,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["delta phi","Blo pr V<",249,1,"3","Bit","0x400","-","Signal : Le module est bloqué par une tension insuffisante."]
["df/dt","ExBlo1-I",250,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["df/dt","ExBlo2-I",250,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["df/dt","ExBlo TripCmd-I",250,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["df/dt","actif",250,1,"3","Bit","0x8","-","Signal : actif"]
["df/dt","ExBlo",250,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["df/dt","Blo TripCmd",250,1,"3","Bit","0x20","-","Signal : Commande de déclenchement bloquée"]
["df/dt","ExBlo TripCmd",250,1,"3","Bit","0x40","-","Signal : Blocage externe de la commande de déclenchement"]
["df/dt","Alarm",250,1,"3","Bit","0x80","-","Signal : Alarme de protection de la fréquence (signal collectif)"]
["df/dt","Décl (*)",250,1,"3","Bit","0x100","-","Signal : Déclenchement de la protection de la fréquence (signal collectif)"]
["df/dt","TripCmd (*)",250,1,"3","Bit","0x200","-","Signal : Commande de déclenchement"]
["df/dt","Blo pr V<",250,1,"3","Bit","0x400","-","Signal : Le module est bloqué par une tension insuffisante."]
["f[1]","ExBlo1-I",34,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["f[1]","ExBlo2-I",34,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["f[1]","ExBlo TripCmd-I",34,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["f[1]","actif",34,1,"3","Bit","0x8","-","Signal : actif"]
["f[1]","ExBlo",34,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["f[1]","Blo pr V<",34,1,"3","Bit","0x20","-","Signal : Le module est bloqué par une tension insuffisante."]
["f[1]","Blo TripCmd",34,1,"3","Bit","0x40","-","Signal : Commande de déclenchement bloquée"]
["f[1]","ExBlo TripCmd",34,1,"3","Bit","0x80","-","Signal : Blocage externe de la commande de déclenchement"]
["f[1]","Alar. f",35,1,"3","Bit","0x1","-","Signal : Alarme de protection de la fréquence"]
["f[1]","Alar. df/dt | DF/DT",35,1,"3","Bit","0x2","-","Alarme de la valeur instantanée ou moyenne de la vitesse de variation de fréquence "]
["f[1]","Déc. f (*)",35,1,"3","Bit","0x4","-","Signal : La fréquence est supérieure à la limite."]
["f[1]","Déc. df/dt | DF/DT (*)",35,1,"3","Bit","0x8","-","Signal : Déclenchement df/dt ou DF/DT"]
["f[1]","Alarm",35,1,"3","Bit","0x10","-","Signal : Alarme de protection de la fréquence (signal collectif)"]
["f[1]","Alarm delta phi",35,1,"3","Bit","0x20","-","Signal : Alarme de saut de vecteur de tension"]
["f[1]","Décl (*)",35,1,"3","Bit","0x40","-","Signal : Déclenchement de la protection de la fréquence (signal collectif)"]
["f[1]","Décl delta phi (*)",35,1,"3","Bit","0x80","-","Signal : Déclenchement sur saut de vecteur de tension"]
["f[1]","TripCmd (*)",35,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["f[2]","ExBlo1-I",36,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["f[2]","ExBlo2-I",36,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["f[2]","ExBlo TripCmd-I",36,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["f[2]","actif",36,1,"3","Bit","0x8","-","Signal : actif"]
["f[2]","ExBlo",36,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["f[2]","Blo pr V<",36,1,"3","Bit","0x20","-","Signal : Le module est bloqué par une tension insuffisante."]
["f[2]","Blo TripCmd",36,1,"3","Bit","0x40","-","Signal : Commande de déclenchement bloquée"]
["f[2]","ExBlo TripCmd",36,1,"3","Bit","0x80","-","Signal : Blocage externe de la commande de déclenchement"]
["f[2]","Alar. f",37,1,"3","Bit","0x1","-","Signal : Alarme de protection de la fréquence"]
["f[2]","Alar. df/dt | DF/DT",37,1,"3","Bit","0x2","-","Alarme de la valeur instantanée ou moyenne de la vitesse de variation de fréquence "]
["f[2]","Déc. f (*)",37,1,"3","Bit","0x4","-","Signal : La fréquence est supérieure à la limite."]
["f[2]","Déc. df/dt | DF/DT (*)",37,1,"3","Bit","0x8","-","Signal : Déclenchement df/dt ou DF/DT"]
["f[2]","Alarm",37,1,"3","Bit","0x10","-","Signal : Alarme de protection de la fréquence (signal collectif)"]
["f[2]","Alarm delta phi",37,1,"3","Bit","0x20","-","Signal : Alarme de saut de vecteur de tension"]
["f[2]","Décl (*)",37,1,"3","Bit","0x40","-","Signal : Déclenchement de la protection de la fréquence (signal collectif)"]
["f[2]","Décl delta phi (*)",37,1,"3","Bit","0x80","-","Signal : Déclenchement sur saut de vecteur de tension"]
["f[2]","TripCmd (*)",37,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["f[3]","ExBlo1-I",38,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["f[3]","ExBlo2-I",38,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["f[3]","ExBlo TripCmd-I",38,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["f[3]","actif",38,1,"3","Bit","0x8","-","Signal : actif"]
["f[3]","ExBlo",38,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["f[3]","Blo pr V<",38,1,"3","Bit","0x20","-","Signal : Le module est bloqué par une tension insuffisante."]
["f[3]","Blo TripCmd",38,1,"3","Bit","0x40","-","Signal : Commande de déclenchement bloquée"]
["f[3]","ExBlo TripCmd",38,1,"3","Bit","0x80","-","Signal : Blocage externe de la commande de déclenchement"]
["f[3]","Alar. f",39,1,"3","Bit","0x1","-","Signal : Alarme de protection de la fréquence"]
["f[3]","Alar. df/dt | DF/DT",39,1,"3","Bit","0x2","-","Alarme de la valeur instantanée ou moyenne de la vitesse de variation de fréquence "]
["f[3]","Déc. f (*)",39,1,"3","Bit","0x4","-","Signal : La fréquence est supérieure à la limite."]
["f[3]","Déc. df/dt | DF/DT (*)",39,1,"3","Bit","0x8","-","Signal : Déclenchement df/dt ou DF/DT"]
["f[3]","Alarm",39,1,"3","Bit","0x10","-","Signal : Alarme de protection de la fréquence (signal collectif)"]
["f[3]","Alarm delta phi",39,1,"3","Bit","0x20","-","Signal : Alarme de saut de vecteur de tension"]
["f[3]","Décl (*)",39,1,"3","Bit","0x40","-","Signal : Déclenchement de la protection de la fréquence (signal collectif)"]
["f[3]","Décl delta phi (*)",39,1,"3","Bit","0x80","-","Signal : Déclenchement sur saut de vecteur de tension"]
["f[3]","TripCmd (*)",39,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["f[4]","ExBlo1-I",40,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["f[4]","ExBlo2-I",40,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["f[4]","ExBlo TripCmd-I",40,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["f[4]","actif",40,1,"3","Bit","0x8","-","Signal : actif"]
["f[4]","ExBlo",40,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["f[4]","Blo pr V<",40,1,"3","Bit","0x20","-","Signal : Le module est bloqué par une tension insuffisante."]
["f[4]","Blo TripCmd",40,1,"3","Bit","0x40","-","Signal : Commande de déclenchement bloquée"]
["f[4]","ExBlo TripCmd",40,1,"3","Bit","0x80","-","Signal : Blocage externe de la commande de déclenchement"]
["f[4]","Alar. f",41,1,"3","Bit","0x1","-","Signal : Alarme de protection de la fréquence"]
["f[4]","Alar. df/dt | DF/DT",41,1,"3","Bit","0x2","-","Alarme de la valeur instantanée ou moyenne de la vitesse de variation de fréquence "]
["f[4]","Déc. f (*)",41,1,"3","Bit","0x4","-","Signal : La fréquence est supérieure à la limite."]
["f[4]","Déc. df/dt | DF/DT (*)",41,1,"3","Bit","0x8","-","Signal : Déclenchement df/dt ou DF/DT"]
["f[4]","Alarm",41,1,"3","Bit","0x10","-","Signal : Alarme de protection de la fréquence (signal collectif)"]
["f[4]","Alarm delta phi",41,1,"3","Bit","0x20","-","Signal : Alarme de saut de vecteur de tension"]
["f[4]","Décl (*)",41,1,"3","Bit","0x40","-","Signal : Déclenchement de la protection de la fréquence (signal collectif)"]
["f[4]","Décl delta phi (*)",41,1,"3","Bit","0x80","-","Signal : Déclenchement sur saut de vecteur de tension"]
["f[4]","TripCmd (*)",41,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["f[5]","ExBlo1-I",42,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["f[5]","ExBlo2-I",42,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["f[5]","ExBlo TripCmd-I",42,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["f[5]","actif",42,1,"3","Bit","0x8","-","Signal : actif"]
["f[5]","ExBlo",42,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["f[5]","Blo pr V<",42,1,"3","Bit","0x20","-","Signal : Le module est bloqué par une tension insuffisante."]
["f[5]","Blo TripCmd",42,1,"3","Bit","0x40","-","Signal : Commande de déclenchement bloquée"]
["f[5]","ExBlo TripCmd",42,1,"3","Bit","0x80","-","Signal : Blocage externe de la commande de déclenchement"]
["f[5]","Alar. f",43,1,"3","Bit","0x1","-","Signal : Alarme de protection de la fréquence"]
["f[5]","Alar. df/dt | DF/DT",43,1,"3","Bit","0x2","-","Alarme de la valeur instantanée ou moyenne de la vitesse de variation de fréquence "]
["f[5]","Déc. f (*)",43,1,"3","Bit","0x4","-","Signal : La fréquence est supérieure à la limite."]
["f[5]","Déc. df/dt | DF/DT (*)",43,1,"3","Bit","0x8","-","Signal : Déclenchement df/dt ou DF/DT"]
["f[5]","Alarm",43,1,"3","Bit","0x10","-","Signal : Alarme de protection de la fréquence (signal collectif)"]
["f[5]","Alarm delta phi",43,1,"3","Bit","0x20","-","Signal : Alarme de saut de vecteur de tension"]
["f[5]","Décl (*)",43,1,"3","Bit","0x40","-","Signal : Déclenchement de la protection de la fréquence (signal collectif)"]
["f[5]","Décl delta phi (*)",43,1,"3","Bit","0x80","-","Signal : Déclenchement sur saut de vecteur de tension"]
["f[5]","TripCmd (*)",43,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]
["f[6]","ExBlo1-I",44,1,"3","Bit","0x1","-","État d'entrée d'un module : Blocage externe1"]
["f[6]","ExBlo2-I",44,1,"3","Bit","0x2","-","État d'entrée d'un module : Blocage externe2"]
["f[6]","ExBlo TripCmd-I",44,1,"3","Bit","0x4","-","État d'entrée d'un module : Blocage externe de la commande de déclenchement"]
["f[6]","actif",44,1,"3","Bit","0x8","-","Signal : actif"]
["f[6]","ExBlo",44,1,"3","Bit","0x10","-","Signal : Blocage externe"]
["f[6]","Blo pr V<",44,1,"3","Bit","0x20","-","Signal : Le module est bloqué par une tension insuffisante."]
["f[6]","Blo TripCmd",44,1,"3","Bit","0x40","-","Signal : Commande de déclenchement bloquée"]
["f[6]","ExBlo TripCmd",44,1,"3","Bit","0x80","-","Signal : Blocage externe de la commande de déclenchement"]
["f[6]","Alar. f",45,1,"3","Bit","0x1","-","Signal : Alarme de protection de la fréquence"]
["f[6]","Alar. df/dt | DF/DT",45,1,"3","Bit","0x2","-","Alarme de la valeur instantanée ou moyenne de la vitesse de variation de fréquence "]
["f[6]","Déc. f (*)",45,1,"3","Bit","0x4","-","Signal : La fréquence est supérieure à la limite."]
["f[6]","Déc. df/dt | DF/DT (*)",45,1,"3","Bit","0x8","-","Signal : Déclenchement df/dt ou DF/DT"]
["f[6]","Alarm",45,1,"3","Bit","0x10","-","Signal : Alarme de protection de la fréquence (signal collectif)"]
["f[6]","Alarm delta phi",45,1,"3","Bit","0x20","-","Signal : Alarme de saut de vecteur de tension"]
["f[6]","Décl (*)",45,1,"3","Bit","0x40","-","Signal : Déclenchement de la protection de la fréquence (signal collectif)"]
["f[6]","Décl delta phi (*)",45,1,"3","Bit","0x80","-","Signal : Déclenchement sur saut de vecteur de tension"]
["f[6]","TripCmd (*)",45,1,"3","Bit","0x100","-","Signal : Commande de déclenchement"]

{"sheet":"Adjust","index":2,"n_rows":13,"n_cols":9,"rows_kept":13,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["Date et heure","o",32500,6,"3 16","Short","Word 0","-","année"]
["Date et heure","m",32500,6,"3 16","Short","Word 1","-","mois"]
["Date et heure","d",32500,6,"3 16","Short","Word 2","-","jours"]
["Date et heure","h",32500,6,"3 16","Short","Word 3","-","heures"]
["Date et heure","min",32500,6,"3 16","Short","Word 4","-","minute"]
["Date et heure","ms",32500,6,"3 16","Short","Word 5","-","millisecondes"]
["Enr déf.","RecordNo",50000,9,"3 16","Short","Word 0","-","Numéro d'enregistrement"]
["Enr déf.","Cause du déclenchement",50000,9,"3 16","Short","Word 1","-","Code de la cause du déclenchement. En présence de plusieurs causes simultanées de déclenchement, la première cause est sélectionnée. Si un autre déclenchement survient par la suite, la nouvelle cause de déclenchement remplace la précédente. Les codes associés aux causes de déclenchement sont fournis dans la documentation SCADA."]
["Enr déf.","Cause de l'excitation",50000,9,"3 16","Short","Word 2","-","Le code pour la cause de la dernière excitation correspond à l'enregistrement du défaut : Consultez la documentation SCADA pour identifier la cause de l'excitation correspondant à ce code"]
["Enr déf.","N° de défaut",50000,9,"3 16","Short","Word 3","-","Nombre de défauts"]
["Enr déf.","Nombre de défauts du réseau",50000,9,"3 16","Short","Word 4","-","Nombre de défauts du réseau : ce module comptabilise tous les défauts (par ex., les alarmes générales »Prot . Alarm«), à l'exception des défaillances qui surviennent lors d'un cycle d'exécution du module de réenclenchement automatique (signal »AR . Running«). (Remarque : le »Fault No.« compte chaque nouveau défaut indépendant des cycles de réenclenchement automatique). En d'autres termes, pour les appareils de protection sans module de réenclenchement automatique, ces deux compteurs sont équivalents."]
["Enr déf.","Marq. tps:",50000,9,"3 16","long long","Word 5- Word 9","-","Marq. Tps en millisecondes depuis 1970 :"]

{"sheet":"Command","index":3,"n_rows":31,"n_cols":9,"rows_kept":31,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["Acquitter","DEL",22000,1,"5","0xFF00","Word 0","-","DEL"]
["Acquitter","Sort binaires",22001,1,"5","0xFF00","Word 0","-","Sort binaires"]
["Acquitter","Scada",22002,1,"5","0xFF00","Word 0","-","Scada"]
["Acquitter","Module",22003,1,"5","0xFF00","Word 0","-","Module"]
["Acquitter","Acq TripCmd",22005,1,"5","0xFF00","Word 0","-","Signal : Acquitter commande de déclenchement"]
["Réini","Compteur diag Modbus",22006,1,"5","0xFF00","Word 0","-","Compteur diag Modbus"]
["Réini","Réin ts cptr éner",22011,1,"5","0xFF00","Word 0","-","Réinitialiser tous les compteurs d'énergie"]
["Scada Cmd","Assbl cmd Scada 1",22020,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 2",22021,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 3",22022,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 4",22023,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 5",22024,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 6",22025,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 7",22026,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 8",22027,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 9",22028,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 10",22029,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 11",22030,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 12",22031,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 13",22032,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 14",22033,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 15",22034,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Scada Cmd","Assbl cmd Scada 16",22035,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Commande Scada affectable"]
["Enr déf.","Res ts enr",22040,1,"5","0xFF00","Word 0","-","Réinitialiser tous les enregistrements"]
["Contac PSet","PS Scada1",22050,1,"5","0xFF00","Word 0","-","Groupe de paramètres Scada 1"]
["Contac PSet","PS Scada2",22051,1,"5","0xFF00","Word 0","-","Groupe de paramètres Scada 2"]
["Contac PSet","PS Scada3",22052,1,"5","0xFF00","Word 0","-","Groupe de paramètres Scada 3"]
["Contac PSet","PS Scada4",22053,1,"5","0xFF00","Word 0","-","Groupe de paramètres Scada 4"]
["Mode AFRMS","AFRMS SCADA",22054,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Signal : Mode SCADA de maintenance de réduction de l'arc électrique"]
["SG","SG ControlCmd1",22100,1,"5","0xFF00=On ~~ 0x0000=Off","Word 0","-","Contrôler l'appareillage de commande"]

{"sheet":"Measure","index":4,"n_rows":272,"n_cols":9,"rows_kept":272,"cut":false,"hidden":false,"merged":[]}
["Module","Subgroup names","Start register","No. of Registers","Function code","Format","Bit Mask / (Bit position)","Unit","Description"]
["AnIn[1]","Val",20896,2,"4","Float IEE754","Word 0","%","Valeur mesurée de l'entrée en pourcentage"]
["AnIn[2]","Val",20900,2,"4","Float IEE754","Word 0","%","Valeur mesurée de l'entrée en pourcentage"]
["Date et heure","o",20000,6,"4","Short","Word 0","-","année"]
["Date et heure","m",20000,6,"4","Short","Word 1","-","mois"]
["Date et heure","d",20000,6,"4","Short","Word 2","-","jours"]
["Date et heure","h",20000,6,"4","Short","Word 3","-","heures"]
["Date et heure","min",20000,6,"4","Short","Word 4","-","minute"]
["Date et heure","ms",20000,6,"4","Short","Word 5","-","millisecondes"]
["IRIG-B","Front",20298,2,"4","Float IEE754","Word 0","-","Fronts : Nombre total de fronts montants et descendants. Ce signal indique si un signal est disponible à l'entrée IRIG-B."]
["IRIG-B","NoOfFrameErrors",20300,2,"4","Float IEE754","Word 0","-","Nombre total d'erreurs de trame.  Trame physiquement corrompue."]
["IRIG-B","NoOfFramesOK",20302,2,"4","Float IEE754","Word 0","-","Nombre total de trames correctes."]
["Modbus","Mes. mappées 1",23000,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 2",23002,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 3",23004,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 4",23006,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 5",23008,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 6",23010,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 7",23012,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 8",23014,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 9",23016,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 10",23018,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 11",23020,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 12",23022,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 13",23024,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 14",23026,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 15",23028,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["Modbus","Mes. mappées 16",23030,2,"4","Float IEE754","Word 0","-","Valeurs des mesurées mappées Vous pouvez utiliser ces valeurs pour fournir les valeurs mesurées au maître Modbus."]
["PQSCr","cos phi ",20152,2,"4","Float IEE754","Word 0","-","Valeur mesurée (calculée) : Facteur de puissance (cos ϕ): Convention de signe: sign(PF) = sign(P )"]
["PQSCr","P  ",20154,2,"4","Float IEE754","Word 0","W","Valeur mesurée (calculée) : Puissance active (P- = puissance active alimentée, P+ = puissance active consommée) (fondamental)"]
["PQSCr","Q  ",20156,2,"4","Float IEE754","Word 0","VAr","Valeur mesurée (calculée) : Puissance réactive (Q- = puissance réactive alimentée, Q+ = puissance réactive consommée) (fondamental)"]
["PQSCr","S  ",20158,2,"4","Float IEE754","Word 0","VA","Valeur mesurée (calculée) : Puissance apparente (fondamental)"]
["PQSCr","Wp+",20174,2,"4","Float IEE754","Word 0","kWh","La puissance active positive est l'énergie active consommée "]
["PQSCr","Wp-",20176,2,"4","Float IEE754","Word 0","kWh","Puissance active négative (énergie alimentée)"]
["PQSCr","Wq+",20178,2,"4","Float IEE754","Word 0","kVArh","La puissance réactive positive est l'énergie réactive consommée"]
["PQSCr","Wq-",20180,2,"4","Float IEE754","Word 0","kVArh","Puissance réactive négative (énergie alimentée)"]
["PQSCr","P  Eff",20452,2,"4","Float IEE754","Word 0","W","Valeur mesurée (calculée) : Puissance active (P- = puissance active alimentée, P+ = puissance active consommée) (Efficace)"]
["PQSCr","S  Eff",20454,2,"4","Float IEE754","Word 0","VA","Valeur mesurée (calculée) : Puissance apparente (Efficace)"]
["PQSCr","cos phi eff",20456,2,"4","Float IEE754","Word 0","-","Valeur mesurée (calculée) : Facteur de puissance (cos ϕ): Convention de signe: sign(PF) = sign(P )"]
["PQSCr","Wp Net",20460,2,"4","Float IEE754","Word 0","kWh","Heures de puissance active absolue"]
["PQSCr","Wq Net",20462,2,"4","Float IEE754","Word 0","kVArh","Heures de puissance réactive absolue"]
["PQSCr","Ws Net",20464,2,"4","Float IEE754","Word 0","kVAh","Heures de puissance apparente absolue"]
["PQSCr","P 1",20496,2,"4","Float IEE754","Word 0","W","Valeur mesurée (calculée) : Puissance active dans le réseau à composante directe (P- = puissance active alimentée, P+ = puissance active consommée)"]
["PQSCr","Q 1",20498,2,"4","Float IEE754","Word 0","VAr","Valeur mesurée (calculée) : Puissance réactive dans le réseau à composante directe (Q- = puissance réactive alimentée, Q+ = puissance réactive consommée)"]
["PQSCr","cos phi max",21092,2,"4","Float IEE754","Word 0","-","Facteur de puissance maximal: Convention de signe: sign(PF) = sign(P )"]
["PQSCr","cos phi min",21094,2,"4","Float IEE754","Word 0","-","Facteur de puissance minimal: Convention de signe: sign(PF) = sign(P )"]
["PQSCr","P moy",21556,2,"4","Float IEE754","Word 0","W","Puissance active moyenne"]
["PQSCr","P max",21558,2,"4","Float IEE754","Word 0","W","Puissance active maximale"]
["PQSCr","P min",21560,2,"4","Float IEE754","Word 0","W","Puissance active minimale"]
["PQSCr","Demand S moy",21562,2,"4","Float IEE754","Word 0","VA","Puissance apparente moyenne"]
["PQSCr","S max",21564,2,"4","Float IEE754","Word 0","VA","Puissance apparente maximale"]
["PQSCr","S min",21566,2,"4","Float IEE754","Word 0","VA","Puissance apparente minimale"]
["PQSCr","cos phi max eff",21570,2,"4","Float IEE754","Word 0","-","Facteur de puissance maximal: Convention de signe: sign(PF) = sign(P )"]
["PQSCr","cos phi min eff",21572,2,"4","Float IEE754","Word 0","-","Facteur de puissance minimal: Convention de signe: sign(PF) = sign(P )"]
["PQSCr","Demand Q moy",21574,2,"4","Float IEE754","Word 0","VAr","Puissance réactive moyenne"]
["PQSCr","Q max",21576,2,"4","Float IEE754","Word 0","VAr","Puissance réactive maximale"]
["PQSCr","Q min",21578,2,"4","Float IEE754","Word 0","VAr","Puissance réactive minimale"]
["PQSCr","Demand Watt crête",21790,2,"4","Float IEE754","Word 0","W","WATTS en crête, WATTS efficaces"]
["PQSCr","Demand VAr crête",21792,2,"4","Float IEE754","Word 0","VAr","VAR en crête, VAR efficace"]
["PQSCr","Demand VA crête",21794,2,"4","Float IEE754","Word 0","VA","VA en crête, VA efficace"]
["PQSCr - valeur de défaut","cos phi ",50152,2,"4","Float IEE754","Word 0","-","Valeur mesurée (calculée) : Facteur de puissance (cos ϕ): Convention de signe: sign(PF) = sign(P ) , telle que stockée dans l’enregistreur de défauts"]
["PQSCr - valeur de défaut","P  ",50154,2,"4","Float IEE754","Word 0","W","Valeur mesurée (calculée) : Puissance active (P- = puissance active alimentée, P+ = puissance active consommée) (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["PQSCr - valeur de défaut","Q  ",50156,2,"4","Float IEE754","Word 0","VAr","Valeur mesurée (calculée) : Puissance réactive (Q- = puissance réactive alimentée, Q+ = puissance réactive consommée) (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["PQSCr - valeur de défaut","S  ",50158,2,"4","Float IEE754","Word 0","VA","Valeur mesurée (calculée) : Puissance apparente (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["PQSCr - valeur de défaut","P  Eff",50452,2,"4","Float IEE754","Word 0","W","Valeur mesurée (calculée) : Puissance active (P- = puissance active alimentée, P+ = puissance active consommée) (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["PQSCr - valeur de défaut","S  Eff",50454,2,"4","Float IEE754","Word 0","VA","Valeur mesurée (calculée) : Puissance apparente (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["PQSCr - valeur de défaut","cos phi eff",50456,2,"4","Float IEE754","Word 0","-","Valeur mesurée (calculée) : Facteur de puissance (cos ϕ): Convention de signe: sign(PF) = sign(P ) , telle que stockée dans l’enregistreur de défauts"]
["PQSCr - valeur de défaut","P 1",50496,2,"4","Float IEE754","Word 0","W","Valeur mesurée (calculée) : Puissance active dans le réseau à composante directe (P- = puissance active alimentée, P+ = puissance active consommée) , telle que stockée dans l’enregistreur de défauts"]
["PQSCr - valeur de défaut","Q 1",50498,2,"4","Float IEE754","Word 0","VAr","Valeur mesurée (calculée) : Puissance réactive dans le réseau à composante directe (Q- = puissance réactive alimentée, Q+ = puissance réactive consommée) , telle que stockée dans l’enregistreur de défauts"]
["SG[1]","Som décl IL1",20800,2,"4","Float IEE754","Word 0","A","Somme des courants de déclenchement de phase "]
["SG[1]","Som décl IL2",20802,2,"4","Float IEE754","Word 0","A","Somme des courants de déclenchement de phase "]
["SG[1]","Som décl IL3",20804,2,"4","Float IEE754","Word 0","A","Somme des courants de déclenchement de phase "]
["SG[1]","Isum Intr /hr",20806,2,"4","Float IEE754","Word 0","kA","Somme par heure des courants de coupure."]
["SG[1]","Capacité CB OUV",20808,2,"4","Float IEE754","Word 0","%","Capacité UTILISÉE du disjoncteur. (100 % signifie que le disjoncteur nécessite une intervention de maintenance.)"]
["SG[1]","TripCmd Cr",20810,2,"4","Float IEE754","Word 0","-","Compteur : nombre total de déclenchements de l’appareillage de connexion"]
["TC","IL1 ",20100,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (fondamental)"]
["TC","IL2 ",20102,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (fondamental)"]
["TC","IL3 ",20104,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (fondamental)"]
["TC","IG mes ",20106,2,"4","Float IEE754","Word 0","A","Valeur mesurée (mesurée) : IG (fondamental)"]
["TC","I0 ",20114,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : Courant nul (fondamental)"]
["TC","I1 ",20116,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : Composante directe du courant (fondamental)"]
["TC","I2 ",20118,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : Courant de charge déséquilibrée (fondamental)"]
["TC","IL1 H2 ",20120,2,"4","Float IEE754","Word 0","%","Valeur mesurée : 2ème harmonique / 1ère harmonique de IL1"]
["TC","IL2 H2 ",20122,2,"4","Float IEE754","Word 0","%","Valeur mesurée : 2ème harmonique / 1ère harmonique de IL2"]
["TC","IL3 H2 ",20124,2,"4","Float IEE754","Word 0","%","Valeur mesurée : 2ème harmonique / 1ère harmonique de IL3"]
["TC","IG H2 mes",20126,2,"4","Float IEE754","Word 0","%","Valeur mesurée : 2ème harmonique / 1ère harmonique de IG (mesurée)"]
["TC","IG calc ",20160,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : IG (fondamental)"]
["TC","phi IG calc",20200,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur de IG calculée\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TC","phi IG mes",20202,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur de IG mesurée\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TC","phi IL1",20204,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur IL1\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TC","phi IL2",20206,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur IL2\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TC","phi IL3",20208,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur IL3\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TC","IL1 THD",20210,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : Courant harmonique total IL1"]
["TC","IL2 THD",20212,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : Courant harmonique total IL2 "]
["TC","IL3 THD",20214,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : Courant harmonique total IL3 "]
["TC","%IL1 THD",20216,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Distorsion harmonique totale IL1"]
["TC","%IL2 THD",20218,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Distorsion harmonique totale IL2 "]
["TC","%IL3 THD",20220,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Distorsion harmonique totale IL3 "]
["TC","IL1 Eff",20316,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (Efficace)"]
["TC","IL2 Eff",20318,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (Efficace)"]
["TC","IL3 Eff",20320,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (Efficace)"]
["TC","IG mes Eff",20322,2,"4","Float IEE754","Word 0","A","Valeur mesurée (mesurée) : IG (Efficace)"]
["TC","IG calc Eff",20324,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : IG (Efficace)"]
["TC","%(I2/I1)",20376,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : I2/I1, l'ordre des phases est automatiquement pris en compte."]
["TC","phi I0",20378,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle de réseau homopolaire\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TC","phi I1",20380,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle de réseau à composante directe\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TC","phi I2",20382,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle de réseau à composante inverse\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TC","IG H2 calc",20500,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : 2ème harmonique / 1ère harmonique de IG (calculée)"]
["TC","I1 max ",21074,2,"4","Float IEE754","Word 0","A","Valeur maximale de la composante directe du courant (fondamental)"]
["TC","I1 min ",21076,2,"4","Float IEE754","Word 0","A","Valeur minimale de la composante directe du courant (fondamental)"]
["TC","I2 max ",21080,2,"4","Float IEE754","Word 0","A","Valeur maximale de la composante inverse (séquence négative) du courant (fondamental)"]
["TC","I2 min  ",21082,2,"4","Float IEE754","Word 0","A","Valeur minimale du courant de charge déséquilibrée (fondamental)"]
["TC","IL1 moy Eff",21130,2,"4","Float IEE754","Word 0","A","Valeur moyenne IL1  (Efficace)"]
["TC","IL2 moy Eff",21132,2,"4","Float IEE754","Word 0","A","Valeur moyenne IL12 (Efficace)"]
["TC","IL3 moy Eff",21134,2,"4","Float IEE754","Word 0","A","Valeur moyenne IL13 (Efficace)"]
["TC","IL1 max Eff",21136,2,"4","Float IEE754","Word 0","A","Valeur maximale IL1  (Efficace)"]
["TC","IL2 max Eff",21138,2,"4","Float IEE754","Word 0","A","Valeur maximale IL12 (Efficace)"]
["TC","IL3 max Eff",21140,2,"4","Float IEE754","Word 0","A","Valeur maximale IL13 (Efficace)"]
["TC","IL1 min  Eff",21142,2,"4","Float IEE754","Word 0","A","Valeur minimale IL1   (Efficace)"]
["TC","IL2 min  Eff",21144,2,"4","Float IEE754","Word 0","A","Valeur minimale IL12  (Efficace)"]
["TC","IL3 min  Eff",21146,2,"4","Float IEE754","Word 0","A","Valeur minimale IL3  (Efficace)"]
["TC","IG H2 mes max",21222,2,"4","Float IEE754","Word 0","%","Valeur mesurée : Rapport maximal entre la 2ème harmonique et la composante fondamentale de IG (mesurée)"]
["TC","IG H2 mes min ",21224,2,"4","Float IEE754","Word 0","%","Valeur mesurée : Rapport minimal entre la 2ème harmonique et la composante fondamentale de IG (mesurée)"]
["TC","IL1 H2 max",21228,2,"4","Float IEE754","Word 0","%","Rapport maximal entre la 2ème harmonique et la composante fondamentale de IL1"]
["TC","IL1 H2 min",21230,2,"4","Float IEE754","Word 0","%","Rapport minimal entre la 2ème harmonique et la composante fondamentale de IL1"]
["TC","IL2 H2 max",21234,2,"4","Float IEE754","Word 0","%","Rapport maximal entre la 2ème harmonique et la composante fondamentale de IL2"]
["TC","IL2 H2 min",21236,2,"4","Float IEE754","Word 0","%","Rapport minimal entre la 2ème harmonique et la composante fondamentale de IL2"]
["TC","IL3 H2 max",21240,2,"4","Float IEE754","Word 0","%","Rapport maximal entre la 2ème harmonique et la composante fondamentale de IL3"]
["TC","IL3 H2 min",21242,2,"4","Float IEE754","Word 0","%","Rapport minimal entre la valeur minimale des 2ème et 1ère harmonique de IL3"]
["TC","IG calc max Eff",21456,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : valeur maximale IG (Efficace)"]
["TC","IG calc min  Eff",21458,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : valeur minimale IG   (Efficace)"]
["TC","IG mes max Eff",21462,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Valeur maximale IG (Efficace)"]
["TC","IG mes min  Eff",21464,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Valeur minimale IG (Efficace)"]
["TC","%(I2/I1)  max",21468,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : I2/I1, valeur maximale, l'ordre des phases est automatiquement pris en compte."]
["TC","%(I2/I1)  min",21470,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : I2/I1, valeur minimale, l'ordre des phases est automatiquement pris en compte."]
["TC","IG H2 calc max",21774,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Rapport maximal entre la 2ème harmonique et la composante fondamentale de IG (calculée)"]
["TC","IG H2 calc min",21776,2,"4","Float IEE754","Word 0","%","IG H2 calc min"]
["TC","Dem IL1 crête",21784,2,"4","Float IEE754","Word 0","A","IL1 en crête, IL1 efficace"]
["TC","Dem IL2 crête",21786,2,"4","Float IEE754","Word 0","A","IL2 en crête, IL2 efficace"]
["TC","Dem IL3 crête",21788,2,"4","Float IEE754","Word 0","A","IL3 en crête, IL3 efficace"]
["TC - valeur de défaut","IL1 ",50100,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IL2 ",50102,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IL3 ",50104,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IG mes ",50106,2,"4","Float IEE754","Word 0","A","Valeur mesurée (mesurée) : IG (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","I0 ",50114,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : Courant nul (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","I1 ",50116,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : Composante directe du courant (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","I2 ",50118,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : Courant de charge déséquilibrée (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IL1 H2 ",50120,2,"4","Float IEE754","Word 0","%","Valeur mesurée : 2ème harmonique / 1ère harmonique de IL1 , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IL2 H2 ",50122,2,"4","Float IEE754","Word 0","%","Valeur mesurée : 2ème harmonique / 1ère harmonique de IL2 , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IL3 H2 ",50124,2,"4","Float IEE754","Word 0","%","Valeur mesurée : 2ème harmonique / 1ère harmonique de IL3 , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IG H2 mes",50126,2,"4","Float IEE754","Word 0","%","Valeur mesurée : 2ème harmonique / 1ère harmonique de IG (mesurée) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IG calc ",50160,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : IG (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","phi IG calc",50200,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur de IG calculée\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","phi IG mes",50202,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur de IG mesurée\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","phi IL1",50204,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur IL1\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","phi IL2",50206,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur IL2\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","phi IL3",50208,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur IL3\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IL1 Eff",50316,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IL2 Eff",50318,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IL3 Eff",50320,2,"4","Float IEE754","Word 0","A","Valeur mesurée : Courant de phase (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IG mes Eff",50322,2,"4","Float IEE754","Word 0","A","Valeur mesurée (mesurée) : IG (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IG calc Eff",50324,2,"4","Float IEE754","Word 0","A","Valeur mesurée (calculée) : IG (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","%(I2/I1)",50376,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : I2/I1, l'ordre des phases est automatiquement pris en compte. , telle que stockée dans l’enregistreur de défauts"]
["TC - valeur de défaut","IG H2 calc",50500,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : 2ème harmonique / 1ère harmonique de IG (calculée) , telle que stockée dans l’enregistreur de défauts"]
["TT","f",20128,2,"4","Float IEE754","Word 0","Hz","Valeur mesurée : Fréquence"]
["TT","VL12 ",20130,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (fondamental)"]
["TT","VL23 ",20132,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (fondamental)"]
["TT","VL31 ",20134,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (fondamental)"]
["TT","VL1 ",20136,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (fondamental)"]
["TT","VL2 ",20138,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (fondamental)"]
["TT","VL3 ",20140,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (fondamental)"]
["TT","VX mes ",20142,2,"4","Float IEE754","Word 0","U","Valeur mesurée (mesurée) : VX mesurée (fondamental)"]
["TT","V0 ",20146,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Composantes symétriques tension résiduelle(fondamental)"]
["TT","V1 ",20148,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Composantes symétriques tension de la composante directe(fondamental)"]
["TT","V2 ",20150,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Composantes symétriques tension de la composante inverse(fondamental)"]
["TT","VG calc ",20162,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : VG (fondamental)"]
["TT","phi VG calc",20386,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur de VG calculée\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi VX mes",20388,2,"4","Float IEE754","Word 0","°","Valeur mesurée : Angle du phaseur de VX mesurée\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi VL12",20390,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL12\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi VL1",20392,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL1\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi VL23",20394,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL23\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi VL2",20396,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL2\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi VL31",20398,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL31\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi VL3",20400,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL3\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi V0",20402,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle de réseau homopolaire\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi V1",20404,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle de réseau à composante directe\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","phi V2",20406,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle de réseau à composante inverse\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée."]
["TT","VL1  THD",20408,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Distorsion harmonique totale VL1 "]
["TT","VL12 THD",20410,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Distorsion harmonique totale V12 "]
["TT","VL2 THD",20412,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Distorsion harmonique totale VL2 "]
["TT","VL23 THD",20414,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Distorsion harmonique totale V23 "]
["TT","VL3 THD",20416,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Distorsion harmonique totale VL3 "]
["TT","VL31 THD",20418,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Distorsion harmonique totale V31 "]
["TT","%VL1  THD",20420,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Distorsion harmonique totale VL1 / Onde directe"]
["TT","%VL12 THD",20422,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Distorsion harmonique totale V12 / Onde directe"]
["TT","%VL2 THD",20424,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Distorsion harmonique totale VL2 / Onde directe"]
["TT","%VL23 THD",20426,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Distorsion harmonique totale V23 / Onde directe"]
["TT","%VL3 THD",20428,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Distorsion harmonique totale VL3 / Onde directe"]
["TT","%VL31 THD",20430,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : Distorsion harmonique totale V31 / Onde directe"]
["TT","VG calc Eff",20432,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : VG (Efficace)"]
["TT","VX mes Eff",20434,2,"4","Float IEE754","Word 0","U","Valeur mesurée (mesurée) : VX mesurée (Efficace)"]
["TT","VL1 Eff",20436,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (Efficace)"]
["TT","VL12 Eff",20438,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (Efficace)"]
["TT","VL2 Eff",20440,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (Efficace)"]
["TT","VL23 Eff",20442,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (Efficace)"]
["TT","VL3 Eff",20444,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (Efficace)"]
["TT","VL31 Eff",20446,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (Efficace)"]
["TT","%(V2/V1)",20450,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : V2/V1, l'ordre des phases est automatiquement pris en compte."]
["TT","f max",21002,2,"4","Float IEE754","Word 0","Hz","Fréquence maxi"]
["TT","f min ",21004,2,"4","Float IEE754","Word 0","Hz","Fréquence mini"]
["TT","V1 max ",21044,2,"4","Float IEE754","Word 0","U","Valeur maximale : Composantes symétriques tension de la composante directe(fondamental)"]
["TT","V1 min ",21046,2,"4","Float IEE754","Word 0","U","Valeur minimale : Composantes symétriques tension de la composante directe(fondamental)"]
["TT","V2 max ",21050,2,"4","Float IEE754","Word 0","U","Valeur maximale : Composantes symétriques tension de la composante inverse(fondamental)"]
["TT","V2 min ",21052,2,"4","Float IEE754","Word 0","U","Valeur minimale : Composantes symétriques tension de la composante inverse(fondamental)"]
["TT","delta phi",21126,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Saut de vecteur de tension"]
["TT","df/dt",21128,2,"4","Float IEE754","Word 0","Hz/s","Valeur mesurée (calculée) : vitesse de variation de la fréquence."]
["TT","VG calc max Eff",21498,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : valeur maximale VX  (Efficace)"]
["TT","VG calc min  Eff",21500,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : valeur minimale VX   (Efficace)"]
["TT","VX mes max Eff",21504,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Valeur maximale VX (Efficace)"]
["TT","VX mes min  Eff",21506,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Valeur minimale VX (Efficace)"]
["TT","VL12 moy Eff",21508,2,"4","Float IEE754","Word 0","U","Valeur moyenne VL12  (Efficace)"]
["TT","VL12 max Eff",21510,2,"4","Float IEE754","Word 0","U","Valeur maximale VL12  (Efficace)"]
["TT","VL12 min  Eff",21512,2,"4","Float IEE754","Word 0","U","Valeur minimale VL12   (Efficace)"]
["TT","VL1 moy Eff",21514,2,"4","Float IEE754","Word 0","U","Valeur moyenne VL1  (Efficace)"]
["TT","VL1 max Eff",21516,2,"4","Float IEE754","Word 0","U","Valeur maximale VL1  (Efficace)"]
["TT","VL1 min  Eff",21518,2,"4","Float IEE754","Word 0","U","Valeur minimale VL1   (Efficace)"]
["TT","VL23 moy Eff",21520,2,"4","Float IEE754","Word 0","U","Valeur moyenne VL23  (Efficace)"]
["TT","VL23 max Eff",21522,2,"4","Float IEE754","Word 0","U","Valeur maximale VL23  (Efficace)"]
["TT","VL23 min  Eff",21524,2,"4","Float IEE754","Word 0","U","Valeur minimale VL23   (Efficace)"]
["TT","VL2 moy Eff",21526,2,"4","Float IEE754","Word 0","U","Valeur moyenne VL2  (Efficace)"]
["TT","VL2 max Eff",21528,2,"4","Float IEE754","Word 0","U","Valeur maximale VL2  (Efficace)"]
["TT","VL2 min  Eff",21530,2,"4","Float IEE754","Word 0","U","Valeur minimale VL2   (Efficace)"]
["TT","VL31 moy Eff",21532,2,"4","Float IEE754","Word 0","U","Valeur moyenne VL31  (Efficace)"]
["TT","VL31 max Eff",21534,2,"4","Float IEE754","Word 0","U","Valeur maximale VL31  (Efficace)"]
["TT","VL31 min  Eff",21536,2,"4","Float IEE754","Word 0","U","Valeur minimale VL31   (Efficace)"]
["TT","VL3 moy Eff",21538,2,"4","Float IEE754","Word 0","U","Valeur moyenne VL3  (Efficace)"]
["TT","VL3 max Eff",21540,2,"4","Float IEE754","Word 0","U","Valeur maximale VL3  (Efficace)"]
["TT","VL3 min  Eff",21542,2,"4","Float IEE754","Word 0","U","Valeur minimale VL3   (Efficace)"]
["TT","%(V2/V1) max",21552,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : valeur maximale V2/V1, l'ordre des phases est automatiquement pris en compte"]
["TT","%(V2/V1) min",21554,2,"4","Float IEE754","Word 0","%","Valeur mesurée (calculée) : valeur minimale V2/V1, l'ordre des phases est automatiquement pris en compte"]
["TT - valeur de défaut","f",50128,2,"4","Float IEE754","Word 0","Hz","Valeur mesurée : Fréquence , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL12 ",50130,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL23 ",50132,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL31 ",50134,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL1 ",50136,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL2 ",50138,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL3 ",50140,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VX mes ",50142,2,"4","Float IEE754","Word 0","U","Valeur mesurée (mesurée) : VX mesurée (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","V0 ",50146,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Composantes symétriques tension résiduelle(fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","V1 ",50148,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Composantes symétriques tension de la composante directe(fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","V2 ",50150,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : Composantes symétriques tension de la composante inverse(fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VG calc ",50162,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : VG (fondamental) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","phi VG calc",50386,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur de VG calculée\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","phi VX mes",50388,2,"4","Float IEE754","Word 0","°","Valeur mesurée : Angle du phaseur de VX mesurée\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","phi VL12",50390,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL12\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","phi VL1",50392,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL1\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","phi VL23",50394,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL23\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","phi VL2",50396,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL2\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","phi VL31",50398,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL31\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","phi VL3",50400,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Angle du phaseur VL3\\nLe phaseur de référence est requis pour le calcul de l'angle. Il s’agit du premier canal de tension (ou courant) mesuré présentant une amplitude suffisamment élevée. , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VG calc Eff",50432,2,"4","Float IEE754","Word 0","U","Valeur mesurée (calculée) : VG (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VX mes Eff",50434,2,"4","Float IEE754","Word 0","U","Valeur mesurée (mesurée) : VX mesurée (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL1 Eff",50436,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL12 Eff",50438,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL2 Eff",50440,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL23 Eff",50442,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL3 Eff",50444,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension phase/neutre (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","VL31 Eff",50446,2,"4","Float IEE754","Word 0","U","Valeur mesurée : Tension entre phases (Efficace) , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","delta phi",51126,2,"4","Float IEE754","Word 0","°","Valeur mesurée (calculée) : Saut de vecteur de tension , telle que stockée dans l’enregistreur de défauts"]
["TT - valeur de défaut","df/dt",51128,2,"4","Float IEE754","Word 0","Hz/s","Valeur mesurée (calculée) : vitesse de variation de la fréquence. , telle que stockée dans l’enregistreur de défauts"]
["Vals","Compi",20008,2,"4","Float IEE754","Word 0","-","Numéro de construction"]
["Vals","Cptr heures fonct",20010,2,"4","Float IEE754","Word 0","h","Compteur d'heures de fonctionnement du module de protection"]

{"sheet":"causeOfTrip","index":5,"n_rows":61,"n_cols":3,"rows_kept":61,"cut":false,"hidden":false,"merged":[]}
["COT modules","COT Code","COT description"]
[null,1,"NORM"]
["AnaP[1]",1001]
["AnaP[2]",1002]
["AnaP[3]",1003]
["AnaP[4]",1004]
["IG[1]",1201]
["IG[2]",1202]
["IG[3]",1203]
["IG[4]",1204]
["ExP[1]",1306]
["ExP[2]",1307]
["ExP[3]",1308]
["ExP[4]",1309]
["Interdéclenchement",1310]
["f[1]",1401]
["f[2]",1402]
["f[3]",1403]
["f[4]",1404]
["f[5]",1405]
["f[6]",1406]
["df/dt",1407]
["delta phi",1408]
["LVRT[1]",2501]
["LVRT[2]",2502]
["I2>[1]",2901]
["I2>[2]",2902]
["V 012[1]",3001]
["V 012[2]",3002]
["V 012[3]",3003]
["V 012[4]",3004]
["V 012[5]",3005]
["V 012[6]",3006]
["I[1]",3201]
["I[2]",3202]
["I[3]",3203]
["I[4]",3204]
["I[5]",3205]
["I[6]",3206]
["PQS[1]",3401]
["PQS[2]",3402]
["PQS[3]",3403]
["PQS[4]",3404]
["PQS[5]",3405]
["PQS[6]",3406]
["Pr",3407]
["Qr",3408]
["PF[1]",3501]
["PF[2]",3502]
["Q->&V<",3601]
["ThR",3801]
["VG[1]",4001]
["VG[2]",4002]
["U[1]",4101]
["U[2]",4102]
["U[3]",4103]
["U[4]",4104]
["U[5]",4105]
["U[6]",4106]
["HVRT[1]",4107]
["HVRT[2]",4108]