## Version
Handoff | SW-Version
61793 | 3.10.a

## State
Module | Subgroup names | Start register | No. of Registers | Function code | Format | Bit Mask / (Bit position) | Unit | Description
AR | Active | 46 | 1 | 3 | Bit | 0x1 | - | Signal: active
AR | ExBlo | 46 | 1 | 3 | Bit | 0x2 | - | Signal: External Blocking
AR | running | 46 | 1 | 3 | Bit | 0x8 | - | Signal: Auto Reclosing running
AR | t-dead | 46 | 1 | 3 | Bit | 0x10 | - | Signal: Dead time between trip and reclosure attempt
AR | successful (*) | 46 | 1 | 3 | Bit | 0x100 | - | Signal: Auto Reclosing successful
AR | failed (*) | 46 | 1 | 3 | Bit | 0x200 | - | Signal: Auto Reclosing failure
AR | t-AR Supervision | 46 | 1 | 3 | Bit | 0x1000 | - | Signal: AR Supervision
AR | ExBlo1-I | 47 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
AR | ExBlo2-I | 47 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
AR | CB ON Cmd | 47 | 1 | 3 | Bit | 0x10 | - | Signal: CB switch ON Command
AR | Pre Shot (*) | 47 | 1 | 3 | Bit | 0x20 | - | Pre Shot Control
AR | Shot 1 (*) | 47 | 1 | 3 | Bit | 0x40 | - | Shot Control
AR | Shot 2 (*) | 47 | 1 | 3 | Bit | 0x80 | - | Shot Control
AR | Shot 3 (*) | 47 | 1 | 3 | Bit | 0x100 | - | Shot Control
AR | Shot 4 (*) | 47 | 1 | 3 | Bit | 0x200 | - | Shot Control
AR | Shot 5 (*) | 47 | 1 | 3 | Bit | 0x400 | - | Shot Control
AR | Shot 6 (*) | 47 | 1 | 3 | Bit | 0x800 | - | Shot Control
AR | Ex Lock-I | 156 | 1 | 3 | Bit | 0x1 | - | Module input state: External AR lockout.
AR | Ex Shot Inc-I | 156 | 1 | 3 | Bit | 0x2 | - | Module input state: The AR Shot counter will be incremented by this external Signal. This can be used for Zone Coordination (of upstream Auto Reclosure devices). Note: This parameter enables the functionality only. The assignment has to be set within the global parameters.
AR | Blo | 156 | 1 | 3 | Bit | 0x4 | - | Signal: Auto Reclosure is blocked
AR | t-Blo after CB man ON | 156 | 1 | 3 | Bit | 0x8 | - | Signal: AR blocked after circuit breaker was switched on manually. This timer will be started if the circuit breaker was switched on manually. While this timer is running, AR cannot be started.
AR | Lock | 156 | 1 | 3 | Bit | 0x10 | - | Signal: Auto Reclosure is locked out
AR | t-Reset Lockout | 156 | 1 | 3 | Bit | 0x20 | - | Signal: Delay Timer for resetting the AR lockout. The reset of the AR lockout state will be delayed for this time, after the reset signal (e.g digital input or Scada) has been detected .
AR | Ready | 156 | 1 | 3 | Bit | 0x40 | - | Signal: Ready to shoot
AR | t-Run2Ready | 156 | 1 | 3 | Bit | 0x80 | - | Signal: Examination Time: If the Circuit Breaker remains after a reclosure attempt for the duration of this timer in the Closed position, the AR has been successful and the AR module returns into the ready state.
AR | Standby | 156 | 1 | 3 | Bit | 0x100 | - | Signal: Standby
AR | Service Alarm 1 | 156 | 1 | 3 | Bit | 0x200 | - | Signal: AR - Service Alarm 1, too many switching operations
AR | Service Alarm 2 | 156 | 1 | 3 | Bit | 0x400 | - | Signal: AR - Service Alarm 2 - too many switching operations
AR | Max Shots / h exceeded | 156 | 1 | 3 | Bit | 0x800 | - | Signal: The maximum allowed number of shots per hour has been exceeded.
BO Slot X2 | BO 1 | 1003 | 1 | 3 | Bit | 0x1 | - | Signal: Binary Output Relay
BO Slot X2 | BO 2 | 1003 | 1 | 3 | Bit | 0x2 | - | Signal: Binary Output Relay
BO Slot X2 | BO 3 | 1003 | 1 | 3 | Bit | 0x4 | - | Signal: Binary Output Relay
BO Slot X2 | BO 4 | 1003 | 1 | 3 | Bit | 0x8 | - | Signal: Binary Output Relay
BO Slot X2 | BO 5 | 1003 | 1 | 3 | Bit | 0x10 | - | Signal: Binary Output Relay
BO Slot X2 | DISARMED! | 1003 | 1 | 3 | Bit | 0x40 | - | Signal: CAUTION! RELAYS DISARMED in order to safely perform maintenance while eliminating the risk of taking an entire process off-line. (Note: The Self Supervision Contact cannot be disarmed). YOU MUST ENSURE that the relays are ARMED AGAIN after maintenance
BO Slot X2 | Outs forced | 1003 | 1 | 3 | Bit | 0x80 | - | Signal: The State of at least one Relay Output has been set by force. That means that the state of at least one Relay is forced and hence does not show the state of the assigned signals.
CBF | ExBlo1-I | 53 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
CBF | ExBlo2-I | 53 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
CBF | Active | 53 | 1 | 3 | Bit | 0x4 | - | Signal: active
CBF | ExBlo | 53 | 1 | 3 | Bit | 0x8 | - | Signal: External Blocking
CBF | Trigger1-I | 53 | 1 | 3 | Bit | 0x10 | - | Module Input: Trigger that will start the CBF
CBF | Trigger2-I | 53 | 1 | 3 | Bit | 0x20 | - | Module Input: Trigger that will start the CBF
CBF | Trigger3-I | 53 | 1 | 3 | Bit | 0x40 | - | Module Input: Trigger that will start the CBF
CBF | running | 53 | 1 | 3 | Bit | 0x80 | - | Signal: CBF-Module started
CBF | Alarm (*) | 53 | 1 | 3 | Bit | 0x100 | - | Signal: Circuit Breaker Failure
CBF | Lockout (*) | 53 | 1 | 3 | Bit | 0x200 | - | Signal: Lockout
CBF | Waiting for Trigger (*) | 53 | 1 | 3 | Bit | 0x400 | - | Waiting for Trigger
CLPU | ExBlo1-I | 66 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking
CLPU | ExBlo2-I | 66 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking
CLPU | Ex rev Interl-I | 66 | 1 | 3 | Bit | 0x4 | - | Module input state: External reverse interlocking
CLPU | Active | 66 | 1 | 3 | Bit | 0x8 | - | Signal: active
CLPU | ExBlo | 66 | 1 | 3 | Bit | 0x10 | - | Signal: External Blocking
CLPU | Ex rev Interl | 66 | 1 | 3 | Bit | 0x20 | - | Signal: External reverse Interlocking
CLPU | enabled | 66 | 1 | 3 | Bit | 0x200 | - | Signal: Cold Load enabled
CLPU | detected (*) | 66 | 1 | 3 | Bit | 0x400 | - | Signal: Cold Load detected
CLPU | I< | 66 | 1 | 3 | Bit | 0x800 | - | Signal: No Load Current.
CLPU | AR Blo | 66 | 1 | 3 | Bit | 0x1000 | - | Signal: Blocked by AR
CLPU | Load Inrush | 66 | 1 | 3 | Bit | 0x2000 | - | Signal: Load Inrush
CLPU | Settle Time | 66 | 1 | 3 | Bit | 0x4000 | - | Signal: Settle Time
CTS | ExBlo1-I | 137 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
CTS | ExBlo2-I | 137 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
CTS | Active | 137 | 1 | 3 | Bit | 0x4 | - | Signal: active
CTS | ExBlo | 137 | 1 | 3 | Bit | 0x8 | - | Signal: External Blocking
CTS | Alarm | 137 | 1 | 3 | Bit | 0x10 | - | Signal: Alarm Current Transformer Measuring Circuit Supervision
Ctrl | Local | 176 | 1 | 3 | Bit | 0x1 | - | Switching Authority: Local
Ctrl | Remote | 176 | 1 | 3 | Bit | 0x2 | - | Switching Authority: Remote
Ctrl | NonInterl | 176 | 1 | 3 | Bit | 0x4 | - | Non-Interlocking is active
Ctrl | SG Disturb | 176 | 1 | 3 | Bit | 0x8 | - | (At least one) Switchgear is disturbed.
Ctrl | SG Indeterm | 176 | 1 | 3 | Bit | 0x10 | - | (At least one) Switchgear is moving (Position cannot be determined).
DI Slot X1 | DI 1 | 1000 | 1 | 3 | Bit | 0x1 | - | Signal: Digital Input
DI Slot X1 | DI 2 | 1000 | 1 | 3 | Bit | 0x2 | - | Signal: Digital Input
DI Slot X1 | DI 3 | 1000 | 1 | 3 | Bit | 0x4 | - | Signal: Digital Input
DI Slot X1 | DI 4 | 1000 | 1 | 3 | Bit | 0x8 | - | Signal: Digital Input
DI Slot X1 | DI 5 | 1000 | 1 | 3 | Bit | 0x10 | - | Signal: Digital Input
DI Slot X1 | DI 6 | 1000 | 1 | 3 | Bit | 0x20 | - | Signal: Digital Input
DI Slot X1 | DI 7 | 1000 | 1 | 3 | Bit | 0x40 | - | Signal: Digital Input
DI Slot X1 | DI 8 | 1000 | 1 | 3 | Bit | 0x80 | - | Signal: Digital Input
ExP[1] | ExBlo1-I | 49 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
ExP[1] | ExBlo2-I | 49 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
ExP[1] | ExBlo TripCmd-I | 49 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
ExP[1] | Alarm-I | 49 | 1 | 3 | Bit | 0x8 | - | Module input state: Alarm
ExP[1] | Trip-I | 49 | 1 | 3 | Bit | 0x10 | - | Module input state: Trip
ExP[1] | Active | 49 | 1 | 3 | Bit | 0x20 | - | Signal: active
ExP[1] | ExBlo | 49 | 1 | 3 | Bit | 0x40 | - | Signal: External Blocking
ExP[1] | Blo TripCmd | 49 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
ExP[1] | ExBlo TripCmd | 49 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
ExP[1] | Alarm | 49 | 1 | 3 | Bit | 0x200 | - | Signal: Alarm
ExP[1] | Trip (*) | 49 | 1 | 3 | Bit | 0x400 | - | Signal: Trip
ExP[1] | TripCmd (*) | 49 | 1 | 3 | Bit | 0x800 | - | Signal: Trip Command
ExP[2] | ExBlo1-I | 50 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
ExP[2] | ExBlo2-I | 50 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
ExP[2] | ExBlo TripCmd-I | 50 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
ExP[2] | Alarm-I | 50 | 1 | 3 | Bit | 0x8 | - | Module input state: Alarm
ExP[2] | Trip-I | 50 | 1 | 3 | Bit | 0x10 | - | Module input state: Trip
ExP[2] | Active | 50 | 1 | 3 | Bit | 0x20 | - | Signal: active
ExP[2] | ExBlo | 50 | 1 | 3 | Bit | 0x40 | - | Signal: External Blocking
ExP[2] | Blo TripCmd | 50 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
ExP[2] | ExBlo TripCmd | 50 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
ExP[2] | Alarm | 50 | 1 | 3 | Bit | 0x200 | - | Signal: Alarm
ExP[2] | Trip (*) | 50 | 1 | 3 | Bit | 0x400 | - | Signal: Trip
ExP[2] | TripCmd (*) | 50 | 1 | 3 | Bit | 0x800 | - | Signal: Trip Command
ExP[3] | ExBlo1-I | 51 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
ExP[3] | ExBlo2-I | 51 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
ExP[3] | ExBlo TripCmd-I | 51 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
ExP[3] | Alarm-I | 51 | 1 | 3 | Bit | 0x8 | - | Module input state: Alarm
ExP[3] | Trip-I | 51 | 1 | 3 | Bit | 0x10 | - | Module input state: Trip
ExP[3] | Active | 51 | 1 | 3 | Bit | 0x20 | - | Signal: active
ExP[3] | ExBlo | 51 | 1 | 3 | Bit | 0x40 | - | Signal: External Blocking
ExP[3] | Blo TripCmd | 51 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
ExP[3] | ExBlo TripCmd | 51 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
ExP[3] | Alarm | 51 | 1 | 3 | Bit | 0x200 | - | Signal: Alarm
ExP[3] | Trip (*) | 51 | 1 | 3 | Bit | 0x400 | - | Signal: Trip
ExP[3] | TripCmd (*) | 51 | 1 | 3 | Bit | 0x800 | - | Signal: Trip Command
ExP[4] | ExBlo1-I | 52 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
ExP[4] | ExBlo2-I | 52 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
ExP[4] | ExBlo TripCmd-I | 52 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
ExP[4] | Alarm-I | 52 | 1 | 3 | Bit | 0x8 | - | Module input state: Alarm
ExP[4] | Trip-I | 52 | 1 | 3 | Bit | 0x10 | - | Module input state: Trip
ExP[4] | Active | 52 | 1 | 3 | Bit | 0x20 | - | Signal: active
ExP[4] | ExBlo | 52 | 1 | 3 | Bit | 0x40 | - | Signal: External Blocking
ExP[4] | Blo TripCmd | 52 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
ExP[4] | ExBlo TripCmd | 52 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
ExP[4] | Alarm | 52 | 1 | 3 | Bit | 0x200 | - | Signal: Alarm
ExP[4] | Trip (*) | 52 | 1 | 3 | Bit | 0x400 | - | Signal: Trip
ExP[4] | TripCmd (*) | 52 | 1 | 3 | Bit | 0x800 | - | Signal: Trip Command
Fast Status Register | Device Type | 5000 | 1 | 3 | Bit | 0xffff | - | Device type code for relationship between device name and its Modbus code. \nHighPROTEC: \nMRI4 - 1000\nMRU4 - 1001\nMRA4 - 1002\nMCA4 - 1003\nMRDT4 - 1005\nMCDTV4 - 1006\nMCDGV4 - 1007\nMRM4 - 1009\nMRMV4 - 1010\nMCDLV4 - 1011
Fast Status Register | Comm Version | 5001 | 1 | 3 | Bit | 0xffff | - | Modbus Communication version. This version number changes if something becomes incompatible between different Modbus releases.
Fast Status Register | Config Bin Inp1-I | 5002 | 1 | 3 | Bit | 0x1 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp2-I | 5002 | 1 | 3 | Bit | 0x2 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp3-I | 5002 | 1 | 3 | Bit | 0x4 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp4-I | 5002 | 1 | 3 | Bit | 0x8 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp5-I | 5002 | 1 | 3 | Bit | 0x10 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp6-I | 5002 | 1 | 3 | Bit | 0x20 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp7-I | 5002 | 1 | 3 | Bit | 0x40 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp8-I | 5002 | 1 | 3 | Bit | 0x80 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp9-I | 5002 | 1 | 3 | Bit | 0x100 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp10-I | 5002 | 1 | 3 | Bit | 0x200 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp11-I | 5002 | 1 | 3 | Bit | 0x400 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp12-I | 5002 | 1 | 3 | Bit | 0x800 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp13-I | 5002 | 1 | 3 | Bit | 0x1000 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp14-I | 5002 | 1 | 3 | Bit | 0x2000 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp15-I | 5002 | 1 | 3 | Bit | 0x4000 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp16-I | 5002 | 1 | 3 | Bit | 0x8000 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp17-I | 5003 | 1 | 3 | Bit | 0x1 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp18-I | 5003 | 1 | 3 | Bit | 0x2 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp19-I | 5003 | 1 | 3 | Bit | 0x4 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp20-I | 5003 | 1 | 3 | Bit | 0x8 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp21-I | 5003 | 1 | 3 | Bit | 0x10 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp22-I | 5003 | 1 | 3 | Bit | 0x20 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp23-I | 5003 | 1 | 3 | Bit | 0x40 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp24-I | 5003 | 1 | 3 | Bit | 0x80 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp25-I | 5003 | 1 | 3 | Bit | 0x100 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp26-I | 5003 | 1 | 3 | Bit | 0x200 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp27-I | 5003 | 1 | 3 | Bit | 0x400 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp28-I | 5003 | 1 | 3 | Bit | 0x800 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp29-I | 5003 | 1 | 3 | Bit | 0x1000 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp30-I | 5003 | 1 | 3 | Bit | 0x2000 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp31-I | 5003 | 1 | 3 | Bit | 0x4000 | - | State of the module input: Config Bin Inp
Fast Status Register | Config Bin Inp32-I | 5003 | 1 | 3 | Bit | 0x8000 | - | State of the module input: Config Bin Inp
Fast Status Register | Trip Cause (*) | 5004 | 1 | 3 | Bit | 0xffff | - | Initial reason of trip. It is presented as an integer value and corresponds to the “Trip” entry in the fault record, which refers to the name of the protective module that tripped first. Look up the definition of these integer values (i. e. the mapping trip code number-->module name) in the “Cause of Trip” table within the SCADA documentation.
I2>[1] | ExBlo1-I | 82 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
I2>[1] | ExBlo2-I | 82 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
I2>[1] | ExBlo TripCmd-I | 82 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
I2>[1] | Active | 82 | 1 | 3 | Bit | 0x8 | - | Signal: active
I2>[1] | ExBlo | 82 | 1 | 3 | Bit | 0x10 | - | Signal: External Blocking
I2>[1] | Blo TripCmd | 82 | 1 | 3 | Bit | 0x20 | - | Signal: Trip Command blocked
I2>[1] | ExBlo TripCmd | 82 | 1 | 3 | Bit | 0x40 | - | Signal: External Blocking of the Trip Command
I2>[1] | Alarm | 82 | 1 | 3 | Bit | 0x80 | - | Signal: Alarm Negative Sequence
I2>[1] | Trip (*) | 82 | 1 | 3 | Bit | 0x100 | - | Signal: Trip
I2>[1] | TripCmd (*) | 82 | 1 | 3 | Bit | 0x200 | - | Signal: Trip Command
I2>[2] | ExBlo1-I | 83 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
I2>[2] | ExBlo2-I | 83 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
I2>[2] | ExBlo TripCmd-I | 83 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
I2>[2] | Active | 83 | 1 | 3 | Bit | 0x8 | - | Signal: active
I2>[2] | ExBlo | 83 | 1 | 3 | Bit | 0x10 | - | Signal: External Blocking
I2>[2] | Blo TripCmd | 83 | 1 | 3 | Bit | 0x20 | - | Signal: Trip Command blocked
I2>[2] | ExBlo TripCmd | 83 | 1 | 3 | Bit | 0x40 | - | Signal: External Blocking of the Trip Command
I2>[2] | Alarm | 83 | 1 | 3 | Bit | 0x80 | - | Signal: Alarm Negative Sequence
I2>[2] | Trip (*) | 83 | 1 | 3 | Bit | 0x100 | - | Signal: Trip
I2>[2] | TripCmd (*) | 83 | 1 | 3 | Bit | 0x200 | - | Signal: Trip Command
IG[1] | ExBlo1-I | 15 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
IG[1] | ExBlo2-I | 15 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
IG[1] | ExBlo TripCmd-I | 15 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
IG[1] | Ex rev Interl-I | 15 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
IG[1] | Active | 15 | 1 | 3 | Bit | 0x10 | - | Signal: active
IG[1] | ExBlo | 15 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
IG[1] | Ex rev Interl | 15 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
IG[1] | Blo TripCmd | 15 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
IG[1] | ExBlo TripCmd | 15 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
IG[1] | IGH2 Blo | 15 | 1 | 3 | Bit | 0x200 | - | Signal: blocked by an inrush
IG[1] | Alarm | 15 | 1 | 3 | Bit | 0x400 | - | Signal: The alarm threshold has been exceeded.
IG[1] | Trip (*) | 15 | 1 | 3 | Bit | 0x800 | - | Signal: Trip
IG[1] | TripCmd (*) | 15 | 1 | 3 | Bit | 0x1000 | - | Signal: Trip Command
IG[2] | ExBlo1-I | 16 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
IG[2] | ExBlo2-I | 16 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
IG[2] | ExBlo TripCmd-I | 16 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
IG[2] | Ex rev Interl-I | 16 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
IG[2] | Active | 16 | 1 | 3 | Bit | 0x10 | - | Signal: active
IG[2] | ExBlo | 16 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
IG[2] | Ex rev Interl | 16 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
IG[2] | Blo TripCmd | 16 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
IG[2] | ExBlo TripCmd | 16 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
IG[2] | IGH2 Blo | 16 | 1 | 3 | Bit | 0x200 | - | Signal: blocked by an inrush
IG[2] | Alarm | 16 | 1 | 3 | Bit | 0x400 | - | Signal: The alarm threshold has been exceeded.
IG[2] | Trip (*) | 16 | 1 | 3 | Bit | 0x800 | - | Signal: Trip
IG[2] | TripCmd (*) | 16 | 1 | 3 | Bit | 0x1000 | - | Signal: Trip Command
IG[3] | ExBlo1-I | 17 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
IG[3] | ExBlo2-I | 17 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
IG[3] | ExBlo TripCmd-I | 17 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
IG[3] | Ex rev Interl-I | 17 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
IG[3] | Active | 17 | 1 | 3 | Bit | 0x10 | - | Signal: active
IG[3] | ExBlo | 17 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
IG[3] | Ex rev Interl | 17 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
IG[3] | Blo TripCmd | 17 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
IG[3] | ExBlo TripCmd | 17 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
IG[3] | IGH2 Blo | 17 | 1 | 3 | Bit | 0x200 | - | Signal: blocked by an inrush
IG[3] | Alarm | 17 | 1 | 3 | Bit | 0x400 | - | Signal: The alarm threshold has been exceeded.
IG[3] | Trip (*) | 17 | 1 | 3 | Bit | 0x800 | - | Signal: Trip
IG[3] | TripCmd (*) | 17 | 1 | 3 | Bit | 0x1000 | - | Signal: Trip Command
IG[4] | ExBlo1-I | 18 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
IG[4] | ExBlo2-I | 18 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
IG[4] | ExBlo TripCmd-I | 18 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
IG[4] | Ex rev Interl-I | 18 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
IG[4] | Active | 18 | 1 | 3 | Bit | 0x10 | - | Signal: active
IG[4] | ExBlo | 18 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
IG[4] | Ex rev Interl | 18 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
IG[4] | Blo TripCmd | 18 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
IG[4] | ExBlo TripCmd | 18 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
IG[4] | IGH2 Blo | 18 | 1 | 3 | Bit | 0x200 | - | Signal: blocked by an inrush
IG[4] | Alarm | 18 | 1 | 3 | Bit | 0x400 | - | Signal: The alarm threshold has been exceeded.
IG[4] | Trip (*) | 18 | 1 | 3 | Bit | 0x800 | - | Signal: Trip
IG[4] | TripCmd (*) | 18 | 1 | 3 | Bit | 0x1000 | - | Signal: Trip Command
IH2 | ExBlo1-I | 22 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
IH2 | ExBlo2-I | 22 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
IH2 | Active | 22 | 1 | 3 | Bit | 0x4 | - | Signal: active
IH2 | ExBlo | 22 | 1 | 3 | Bit | 0x8 | - | Signal: External Blocking
IH2 | Blo L1 | 22 | 1 | 3 | Bit | 0x10 | - | Signal: Blocked L1
IH2 | Blo L2 | 22 | 1 | 3 | Bit | 0x20 | - | Signal: Blocked L2
IH2 | Blo L3 | 22 | 1 | 3 | Bit | 0x40 | - | Signal: Blocked L3
IH2 | Blo IG meas | 22 | 1 | 3 | Bit | 0x80 | - | Signal: Blocking of the ground (earth) protection module (measured ground current)
IH2 | 3-ph Blo | 22 | 1 | 3 | Bit | 0x100 | - | Signal: Inrush was detected in at least one phase - trip command blocked.
IH2 | Blo IG calc | 22 | 1 | 3 | Bit | 0x200 | - | Signal: Blocking of the ground (earth) protection module (calculated ground current)
IRIG-B | IRIG-B active | 148 | 1 | 3 | Bit | 0x1 | - | Signal: If there is no valid IRIG-B signal for 60 sec, IRIG-B is regarded as inactive.
IRIG-B | High-Low Invert | 148 | 1 | 3 | Bit | 0x2 | - | Signal: The High and Low signals of the IRIG-B are inverted. This does NOT mean that the wiring is faulty. If the wiring is faulty no IRIG-B signal will be detected.
I[1] | ExBlo1-I | 3 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
I[1] | ExBlo2-I | 3 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
I[1] | ExBlo TripCmd-I | 3 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
I[1] | Ex rev Interl-I | 3 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
I[1] | Active | 3 | 1 | 3 | Bit | 0x10 | - | Signal: active
I[1] | ExBlo | 3 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
I[1] | Ex rev Interl | 3 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
I[1] | Blo TripCmd | 3 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
I[1] | ExBlo TripCmd | 3 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
I[1] | IH2 Blo | 3 | 1 | 3 | Bit | 0x200 | - | Signal: Blocking the trip command by an inrush
I[1] | Alarm L1 | 4 | 1 | 3 | Bit | 0x1 | - | Signal: Alarm L1
I[1] | Alarm L2 | 4 | 1 | 3 | Bit | 0x2 | - | Signal: Alarm L2
I[1] | Alarm L3 | 4 | 1 | 3 | Bit | 0x4 | - | Signal: Alarm L3
I[1] | Alarm | 4 | 1 | 3 | Bit | 0x8 | - | Signal: Alarm
I[1] | Trip L1 (*) | 4 | 1 | 3 | Bit | 0x10 | - | Signal: General Trip Phase L1
I[1] | Trip L2 (*) | 4 | 1 | 3 | Bit | 0x20 | - | Signal: General Trip Phase L2
I[1] | Trip L3 (*) | 4 | 1 | 3 | Bit | 0x40 | - | Signal: General Trip Phase L3
I[1] | Trip (*) | 4 | 1 | 3 | Bit | 0x80 | - | Signal: Trip
I[1] | TripCmd (*) | 4 | 1 | 3 | Bit | 0x100 | - | Signal: Trip Command
I[2] | ExBlo1-I | 5 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
I[2] | ExBlo2-I | 5 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
I[2] | ExBlo TripCmd-I | 5 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
I[2] | Ex rev Interl-I | 5 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
I[2] | Active | 5 | 1 | 3 | Bit | 0x10 | - | Signal: active
I[2] | ExBlo | 5 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
I[2] | Ex rev Interl | 5 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
I[2] | Blo TripCmd | 5 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
I[2] | ExBlo TripCmd | 5 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
I[2] | IH2 Blo | 5 | 1 | 3 | Bit | 0x200 | - | Signal: Blocking the trip command by an inrush
I[2] | Alarm L1 | 6 | 1 | 3 | Bit | 0x1 | - | Signal: Alarm L1
I[2] | Alarm L2 | 6 | 1 | 3 | Bit | 0x2 | - | Signal: Alarm L2
I[2] | Alarm L3 | 6 | 1 | 3 | Bit | 0x4 | - | Signal: Alarm L3
I[2] | Alarm | 6 | 1 | 3 | Bit | 0x8 | - | Signal: Alarm
I[2] | Trip L1 (*) | 6 | 1 | 3 | Bit | 0x10 | - | Signal: General Trip Phase L1
I[2] | Trip L2 (*) | 6 | 1 | 3 | Bit | 0x20 | - | Signal: General Trip Phase L2
I[2] | Trip L3 (*) | 6 | 1 | 3 | Bit | 0x40 | - | Signal: General Trip Phase L3
I[2] | Trip (*) | 6 | 1 | 3 | Bit | 0x80 | - | Signal: Trip
I[2] | TripCmd (*) | 6 | 1 | 3 | Bit | 0x100 | - | Signal: Trip Command
I[3] | ExBlo1-I | 7 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
I[3] | ExBlo2-I | 7 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
I[3] | ExBlo TripCmd-I | 7 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
I[3] | Ex rev Interl-I | 7 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
I[3] | Active | 7 | 1 | 3 | Bit | 0x10 | - | Signal: active
I[3] | ExBlo | 7 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
I[3] | Ex rev Interl | 7 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
I[3] | Blo TripCmd | 7 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
I[3] | ExBlo TripCmd | 7 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
I[3] | IH2 Blo | 7 | 1 | 3 | Bit | 0x200 | - | Signal: Blocking the trip command by an inrush
I[3] | Alarm L1 | 8 | 1 | 3 | Bit | 0x1 | - | Signal: Alarm L1
I[3] | Alarm L2 | 8 | 1 | 3 | Bit | 0x2 | - | Signal: Alarm L2
I[3] | Alarm L3 | 8 | 1 | 3 | Bit | 0x4 | - | Signal: Alarm L3
I[3] | Alarm | 8 | 1 | 3 | Bit | 0x8 | - | Signal: Alarm
I[3] | Trip L1 (*) | 8 | 1 | 3 | Bit | 0x10 | - | Signal: General Trip Phase L1
I[3] | Trip L2 (*) | 8 | 1 | 3 | Bit | 0x20 | - | Signal: General Trip Phase L2
I[3] | Trip L3 (*) | 8 | 1 | 3 | Bit | 0x40 | - | Signal: General Trip Phase L3
I[3] | Trip (*) | 8 | 1 | 3 | Bit | 0x80 | - | Signal: Trip
I[3] | TripCmd (*) | 8 | 1 | 3 | Bit | 0x100 | - | Signal: Trip Command
I[4] | ExBlo1-I | 9 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
I[4] | ExBlo2-I | 9 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
I[4] | ExBlo TripCmd-I | 9 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
I[4] | Ex rev Interl-I | 9 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
I[4] | Active | 9 | 1 | 3 | Bit | 0x10 | - | Signal: active
I[4] | ExBlo | 9 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
I[4] | Ex rev Interl | 9 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
I[4] | Blo TripCmd | 9 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
I[4] | ExBlo TripCmd | 9 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
I[4] | IH2 Blo | 9 | 1 | 3 | Bit | 0x200 | - | Signal: Blocking the trip command by an inrush
I[4] | Alarm L1 | 10 | 1 | 3 | Bit | 0x1 | - | Signal: Alarm L1
I[4] | Alarm L2 | 10 | 1 | 3 | Bit | 0x2 | - | Signal: Alarm L2
I[4] | Alarm L3 | 10 | 1 | 3 | Bit | 0x4 | - | Signal: Alarm L3
I[4] | Alarm | 10 | 1 | 3 | Bit | 0x8 | - | Signal: Alarm
I[4] | Trip L1 (*) | 10 | 1 | 3 | Bit | 0x10 | - | Signal: General Trip Phase L1
I[4] | Trip L2 (*) | 10 | 1 | 3 | Bit | 0x20 | - | Signal: General Trip Phase L2
I[4] | Trip L3 (*) | 10 | 1 | 3 | Bit | 0x40 | - | Signal: General Trip Phase L3
I[4] | Trip (*) | 10 | 1 | 3 | Bit | 0x80 | - | Signal: Trip
I[4] | TripCmd (*) | 10 | 1 | 3 | Bit | 0x100 | - | Signal: Trip Command
I[5] | ExBlo1-I | 11 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
I[5] | ExBlo2-I | 11 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
I[5] | ExBlo TripCmd-I | 11 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
I[5] | Ex rev Interl-I | 11 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
I[5] | Active | 11 | 1 | 3 | Bit | 0x10 | - | Signal: active
I[5] | ExBlo | 11 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
I[5] | Ex rev Interl | 11 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
I[5] | Blo TripCmd | 11 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
I[5] | ExBlo TripCmd | 11 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
I[5] | IH2 Blo | 11 | 1 | 3 | Bit | 0x200 | - | Signal: Blocking the trip command by an inrush
I[5] | Alarm L1 | 12 | 1 | 3 | Bit | 0x1 | - | Signal: Alarm L1
I[5] | Alarm L2 | 12 | 1 | 3 | Bit | 0x2 | - | Signal: Alarm L2
I[5] | Alarm L3 | 12 | 1 | 3 | Bit | 0x4 | - | Signal: Alarm L3
I[5] | Alarm | 12 | 1 | 3 | Bit | 0x8 | - | Signal: Alarm
I[5] | Trip L1 (*) | 12 | 1 | 3 | Bit | 0x10 | - | Signal: General Trip Phase L1
I[5] | Trip L2 (*) | 12 | 1 | 3 | Bit | 0x20 | - | Signal: General Trip Phase L2
I[5] | Trip L3 (*) | 12 | 1 | 3 | Bit | 0x40 | - | Signal: General Trip Phase L3
I[5] | Trip (*) | 12 | 1 | 3 | Bit | 0x80 | - | Signal: Trip
I[5] | TripCmd (*) | 12 | 1 | 3 | Bit | 0x100 | - | Signal: Trip Command
I[6] | ExBlo1-I | 13 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
I[6] | ExBlo2-I | 13 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
I[6] | ExBlo TripCmd-I | 13 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
I[6] | Ex rev Interl-I | 13 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
I[6] | Active | 13 | 1 | 3 | Bit | 0x10 | - | Signal: active
I[6] | ExBlo | 13 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
I[6] | Ex rev Interl | 13 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
I[6] | Blo TripCmd | 13 | 1 | 3 | Bit | 0x80 | - | Signal: Trip Command blocked
I[6] | ExBlo TripCmd | 13 | 1 | 3 | Bit | 0x100 | - | Signal: External Blocking of the Trip Command
I[6] | IH2 Blo | 13 | 1 | 3 | Bit | 0x200 | - | Signal: Blocking the trip command by an inrush
I[6] | Alarm L1 | 14 | 1 | 3 | Bit | 0x1 | - | Signal: Alarm L1
I[6] | Alarm L2 | 14 | 1 | 3 | Bit | 0x2 | - | Signal: Alarm L2
I[6] | Alarm L3 | 14 | 1 | 3 | Bit | 0x4 | - | Signal: Alarm L3
I[6] | Alarm | 14 | 1 | 3 | Bit | 0x8 | - | Signal: Alarm
I[6] | Trip L1 (*) | 14 | 1 | 3 | Bit | 0x10 | - | Signal: General Trip Phase L1
I[6] | Trip L2 (*) | 14 | 1 | 3 | Bit | 0x20 | - | Signal: General Trip Phase L2
I[6] | Trip L3 (*) | 14 | 1 | 3 | Bit | 0x40 | - | Signal: General Trip Phase L3
I[6] | Trip (*) | 14 | 1 | 3 | Bit | 0x80 | - | Signal: Trip
I[6] | TripCmd (*) | 14 | 1 | 3 | Bit | 0x100 | - | Signal: Trip Command
Logics | LE1.Gate Out | 1100 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE1.Timer Out | 1100 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE1.Out | 1100 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE1.Out inverted | 1100 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE1.Gate In1-I | 1100 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE1.Gate In2-I | 1100 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE1.Gate In3-I | 1100 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE1.Gate In4-I | 1100 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE1.Reset Latch-I | 1100 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE2.Gate Out | 1101 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE2.Timer Out | 1101 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE2.Out | 1101 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE2.Out inverted | 1101 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE2.Gate In1-I | 1101 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE2.Gate In2-I | 1101 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE2.Gate In3-I | 1101 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE2.Gate In4-I | 1101 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE2.Reset Latch-I | 1101 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE3.Gate Out | 1102 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE3.Timer Out | 1102 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE3.Out | 1102 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE3.Out inverted | 1102 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE3.Gate In1-I | 1102 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE3.Gate In2-I | 1102 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE3.Gate In3-I | 1102 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE3.Gate In4-I | 1102 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE3.Reset Latch-I | 1102 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE4.Gate Out | 1103 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE4.Timer Out | 1103 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE4.Out | 1103 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE4.Out inverted | 1103 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE4.Gate In1-I | 1103 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE4.Gate In2-I | 1103 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE4.Gate In3-I | 1103 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE4.Gate In4-I | 1103 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE4.Reset Latch-I | 1103 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE5.Gate Out | 1104 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE5.Timer Out | 1104 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE5.Out | 1104 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE5.Out inverted | 1104 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE5.Gate In1-I | 1104 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE5.Gate In2-I | 1104 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE5.Gate In3-I | 1104 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE5.Gate In4-I | 1104 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE5.Reset Latch-I | 1104 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE6.Gate Out | 1105 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE6.Timer Out | 1105 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE6.Out | 1105 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE6.Out inverted | 1105 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE6.Gate In1-I | 1105 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE6.Gate In2-I | 1105 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE6.Gate In3-I | 1105 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE6.Gate In4-I | 1105 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE6.Reset Latch-I | 1105 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE7.Gate Out | 1106 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE7.Timer Out | 1106 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE7.Out | 1106 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE7.Out inverted | 1106 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE7.Gate In1-I | 1106 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE7.Gate In2-I | 1106 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE7.Gate In3-I | 1106 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE7.Gate In4-I | 1106 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE7.Reset Latch-I | 1106 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE8.Gate Out | 1107 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE8.Timer Out | 1107 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE8.Out | 1107 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE8.Out inverted | 1107 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE8.Gate In1-I | 1107 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE8.Gate In2-I | 1107 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE8.Gate In3-I | 1107 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE8.Gate In4-I | 1107 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE8.Reset Latch-I | 1107 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE9.Gate Out | 1108 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE9.Timer Out | 1108 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE9.Out | 1108 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE9.Out inverted | 1108 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE9.Gate In1-I | 1108 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE9.Gate In2-I | 1108 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE9.Gate In3-I | 1108 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE9.Gate In4-I | 1108 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE9.Reset Latch-I | 1108 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE10.Gate Out | 1109 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE10.Timer Out | 1109 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE10.Out | 1109 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE10.Out inverted | 1109 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE10.Gate In1-I | 1109 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE10.Gate In2-I | 1109 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE10.Gate In3-I | 1109 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE10.Gate In4-I | 1109 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE10.Reset Latch-I | 1109 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE11.Gate Out | 1110 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE11.Timer Out | 1110 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE11.Out | 1110 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE11.Out inverted | 1110 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE11.Gate In1-I | 1110 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE11.Gate In2-I | 1110 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE11.Gate In3-I | 1110 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE11.Gate In4-I | 1110 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE11.Reset Latch-I | 1110 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE12.Gate Out | 1111 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE12.Timer Out | 1111 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE12.Out | 1111 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE12.Out inverted | 1111 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE12.Gate In1-I | 1111 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE12.Gate In2-I | 1111 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE12.Gate In3-I | 1111 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE12.Gate In4-I | 1111 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE12.Reset Latch-I | 1111 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE13.Gate Out | 1112 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE13.Timer Out | 1112 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE13.Out | 1112 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE13.Out inverted | 1112 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE13.Gate In1-I | 1112 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE13.Gate In2-I | 1112 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE13.Gate In3-I | 1112 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE13.Gate In4-I | 1112 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE13.Reset Latch-I | 1112 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE14.Gate Out | 1113 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE14.Timer Out | 1113 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE14.Out | 1113 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE14.Out inverted | 1113 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE14.Gate In1-I | 1113 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE14.Gate In2-I | 1113 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE14.Gate In3-I | 1113 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE14.Gate In4-I | 1113 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE14.Reset Latch-I | 1113 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE15.Gate Out | 1114 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE15.Timer Out | 1114 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE15.Out | 1114 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE15.Out inverted | 1114 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE15.Gate In1-I | 1114 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE15.Gate In2-I | 1114 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE15.Gate In3-I | 1114 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE15.Gate In4-I | 1114 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE15.Reset Latch-I | 1114 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE16.Gate Out | 1115 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE16.Timer Out | 1115 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE16.Out | 1115 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE16.Out inverted | 1115 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE16.Gate In1-I | 1115 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE16.Gate In2-I | 1115 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE16.Gate In3-I | 1115 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE16.Gate In4-I | 1115 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE16.Reset Latch-I | 1115 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE17.Gate Out | 1116 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE17.Timer Out | 1116 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE17.Out | 1116 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE17.Out inverted | 1116 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE17.Gate In1-I | 1116 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE17.Gate In2-I | 1116 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE17.Gate In3-I | 1116 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE17.Gate In4-I | 1116 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE17.Reset Latch-I | 1116 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE18.Gate Out | 1117 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE18.Timer Out | 1117 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE18.Out | 1117 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE18.Out inverted | 1117 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE18.Gate In1-I | 1117 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE18.Gate In2-I | 1117 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE18.Gate In3-I | 1117 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE18.Gate In4-I | 1117 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE18.Reset Latch-I | 1117 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE19.Gate Out | 1118 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE19.Timer Out | 1118 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE19.Out | 1118 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE19.Out inverted | 1118 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE19.Gate In1-I | 1118 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE19.Gate In2-I | 1118 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE19.Gate In3-I | 1118 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE19.Gate In4-I | 1118 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE19.Reset Latch-I | 1118 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Logics | LE20.Gate Out | 1119 | 1 | 3 | Bit | 0x1 | - | Signal: Output of the logic gate
Logics | LE20.Timer Out | 1119 | 1 | 3 | Bit | 0x2 | - | Signal: Timer Output
Logics | LE20.Out | 1119 | 1 | 3 | Bit | 0x4 | - | Signal: Latched Output (Q)
Logics | LE20.Out inverted | 1119 | 1 | 3 | Bit | 0x8 | - | Signal: Negated Latched Output (Q NOT)
Logics | LE20.Gate In1-I | 1119 | 1 | 3 | Bit | 0x10 | - | State of the module input: Assignment of the Input Signal
Logics | LE20.Gate In2-I | 1119 | 1 | 3 | Bit | 0x20 | - | State of the module input: Assignment of the Input Signal
Logics | LE20.Gate In3-I | 1119 | 1 | 3 | Bit | 0x40 | - | State of the module input: Assignment of the Input Signal
Logics | LE20.Gate In4-I | 1119 | 1 | 3 | Bit | 0x80 | - | State of the module input: Assignment of the Input Signal
Logics | LE20.Reset Latch-I | 1119 | 1 | 3 | Bit | 0x100 | - | State of the module input: Reset Signal for the Latching
Modbus | Scada Cmd 1 | 1005 | 1 | 3 | Bit | 0x1 | - | Scada Command
Modbus | Scada Cmd 2 | 1005 | 1 | 3 | Bit | 0x2 | - | Scada Command
Modbus | Scada Cmd 3 | 1005 | 1 | 3 | Bit | 0x4 | - | Scada Command
Modbus | Scada Cmd 4 | 1005 | 1 | 3 | Bit | 0x8 | - | Scada Command
Modbus | Scada Cmd 5 | 1005 | 1 | 3 | Bit | 0x10 | - | Scada Command
Modbus | Scada Cmd 6 | 1005 | 1 | 3 | Bit | 0x20 | - | Scada Command
Modbus | Scada Cmd 7 | 1005 | 1 | 3 | Bit | 0x40 | - | Scada Command
Modbus | Scada Cmd 8 | 1005 | 1 | 3 | Bit | 0x80 | - | Scada Command
Modbus | Scada Cmd 9 | 1005 | 1 | 3 | Bit | 0x100 | - | Scada Command
Modbus | Scada Cmd 10 | 1005 | 1 | 3 | Bit | 0x200 | - | Scada Command
Modbus | Scada Cmd 11 | 1005 | 1 | 3 | Bit | 0x400 | - | Scada Command
Modbus | Scada Cmd 12 | 1005 | 1 | 3 | Bit | 0x800 | - | Scada Command
Modbus | Scada Cmd 13 | 1005 | 1 | 3 | Bit | 0x1000 | - | Scada Command
Modbus | Scada Cmd 14 | 1005 | 1 | 3 | Bit | 0x2000 | - | Scada Command
Modbus | Scada Cmd 15 | 1005 | 1 | 3 | Bit | 0x4000 | - | Scada Command
Modbus | Scada Cmd 16 | 1005 | 1 | 3 | Bit | 0x8000 | - | Scada Command
PSet-Switch | PS 1 | 59 | 1 | 3 | Bit | 0x1 | - | Signal: The currently active Parameter Set is PS 1
PSet-Switch | PS 2 | 59 | 1 | 3 | Bit | 0x2 | - | Signal: The currently active Parameter Set is PS 2
PSet-Switch | PS 3 | 59 | 1 | 3 | Bit | 0x4 | - | Signal: The currently active Parameter Set is PS 3
PSet-Switch | PS 4 | 59 | 1 | 3 | Bit | 0x8 | - | Signal: The currently active Parameter Set is PS 4
PSet-Switch | PSS manual | 59 | 1 | 3 | Bit | 0x10 | - | Signal: Manual Switch over of a Parameter Set
PSet-Switch | PSS via Scada | 59 | 1 | 3 | Bit | 0x20 | - | Signal: Parameter Set Switch via Scada. Write into this output byte the integer of the parameter set that should become active (e.g. 4 => Switch onto parameter set 4).
PSet-Switch | PSS via Inp fct | 59 | 1 | 3 | Bit | 0x40 | - | Signal: Parameter Set Switch via input function
PSet-Switch | PS1-I | 59 | 1 | 3 | Bit | 0x80 | - | State of the module input respectively of the signal, that should activate this Parameter Setting Group.
PSet-Switch | PS2-I | 59 | 1 | 3 | Bit | 0x100 | - | State of the module input respectively of the signal, that should activate this Parameter Setting Group.
PSet-Switch | PS3-I | 59 | 1 | 3 | Bit | 0x200 | - | State of the module input respectively of the signal, that should activate this Parameter Setting Group.
PSet-Switch | PS4-I | 59 | 1 | 3 | Bit | 0x400 | - | State of the module input respectively of the signal, that should activate this Parameter Setting Group.
PSet-Switch | min 1 param changed (*) | 59 | 1 | 3 | Bit | 0x800 | - | Signal: At least one parameter has been changed
Prot | ExBlo1-I | 1 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
Prot | ExBlo2-I | 1 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
Prot | Active | 1 | 1 | 3 | Bit | 0x4 | - | Signal: active
Prot | ExBlo | 1 | 1 | 3 | Bit | 0x8 | - | Signal: External Blocking
Prot | Alarm L1 | 1 | 1 | 3 | Bit | 0x10 | - | Signal: General-Alarm L1
Prot | Alarm L2 | 1 | 1 | 3 | Bit | 0x20 | - | Signal: General-Alarm L2
Prot | Alarm L3 | 1 | 1 | 3 | Bit | 0x40 | - | Signal: General-Alarm L3
Prot | Alarm G | 1 | 1 | 3 | Bit | 0x80 | - | Signal: General-Alarm - Earth fault
Prot | Alarm | 1 | 1 | 3 | Bit | 0x100 | - | Signal: General Alarm
Prot | Trip L1 (*) | 1 | 1 | 3 | Bit | 0x200 | - | Signal: General Trip L1
Prot | Trip L2 (*) | 1 | 1 | 3 | Bit | 0x400 | - | Signal: General Trip L2
Prot | Trip L3 (*) | 1 | 1 | 3 | Bit | 0x800 | - | Signal: General Trip L3
Prot | Trip G (*) | 1 | 1 | 3 | Bit | 0x1000 | - | Signal: General Trip Ground fault
Prot | Trip (*) | 1 | 1 | 3 | Bit | 0x2000 | - | Signal: General Trip
Prot | Blo TripCmd | 2 | 1 | 3 | Bit | 0x1 | - | Signal: Trip Command blocked
Prot | ExBlo TripCmd-I | 2 | 1 | 3 | Bit | 0x2 | - | Module input state: External Blocking of the Trip Command
Prot | ExBlo TripCmd | 2 | 1 | 3 | Bit | 0x4 | - | Signal: External Blocking of the Trip Command
Prot | Fault No. | 57 | 1 | 3 | Bit | 0xffff | - | Fault number
Prot | No. of Grid Faults | 58 | 1 | 3 | Bit | 0xffff | - | Number of grid faults: This is a counter for all faults (i.e. General Alarms »Prot . Alarm«), but except faults during a running cycle of the Automatic Reclosure module (signal »AR . running«). (Remark: The »Fault No.« counts every new fault independent of AR cycles. This means that for protective devices without AR module these two counters are equivalent.)
SG[1] | Aux OFF-I | 177 | 1 | 3 | Bit | 0x1 | - | Module input state: Position indicator/check-back signal of the CB (52b)
SG[1] | Aux ON-I | 177 | 1 | 3 | Bit | 0x2 | - | Module Input State: Position indicator/check-back signal of the CB (52a)
SG[1] | Ready-I | 177 | 1 | 3 | Bit | 0x4 | - | Module input state: CB ready
SG[1] | Sys-in-Sync-I | 177 | 1 | 3 | Bit | 0x8 | - | State of the module input: This signals has to become true within the synchronization time. If not, switching is unsuccessful.
SG[1] | Interl OFF1-I | 177 | 1 | 3 | Bit | 0x10 | - | State of the module input: Interlocking of the OFF command
SG[1] | Interl OFF2-I | 177 | 1 | 3 | Bit | 0x20 | - | State of the module input: Interlocking of the OFF command
SG[1] | Interl OFF3-I | 177 | 1 | 3 | Bit | 0x40 | - | State of the module input: Interlocking of the OFF command
SG[1] | Interl ON1-I | 177 | 1 | 3 | Bit | 0x80 | - | State of the module input: Interlocking of the ON command
SG[1] | Interl ON2-I | 177 | 1 | 3 | Bit | 0x100 | - | State of the module input: Interlocking of the ON command
SG[1] | Interl ON3-I | 177 | 1 | 3 | Bit | 0x200 | - | State of the module input: Interlocking of the ON command
SG[1] | SCmd OFF-I | 177 | 1 | 3 | Bit | 0x800 | - | State of the module input: Switching OFF Command, e.g. the state of the Logics or the state of the digital input
SG[1] | SCmd ON-I | 177 | 1 | 3 | Bit | 0x1000 | - | State of the module input: Switching ON Command, e.g. the state of the Logics or the state of the digital input
SG[1] | TripCmd (*) | 177 | 1 | 3 | Bit | 0x2000 | - | Signal: Trip Command
SG[1] | OFF Cmd | 177 | 1 | 3 | Bit | 0x4000 | - | Signal: OFF Command issued to the switchgear. Depending on the setting the signal may include the OFF command of the Prot module.
SG[1] | OFF Cmd manual | 177 | 1 | 3 | Bit | 0x8000 | - | Signal: OFF Cmd manual
SG[1] | ON Cmd | 178 | 1 | 3 | Bit | 0x1 | - | Signal: ON Command issued to the switchgear. Depending on the setting the signal may include the ON command of the Prot module.
SG[1] | ON Cmd manual | 178 | 1 | 3 | Bit | 0x2 | - | Signal: ON Cmd manual
SG[1] | Sync ON request | 178 | 1 | 3 | Bit | 0x4 | - | Signal: Synchronous ON request
SG[1] | SGwear Slow SG | 178 | 1 | 3 | Bit | 0x8 | - | Signal: Alarm, the circuit breaker (load-break switch) becomes slower
SG[1] | Res SGwear Sl SG | 178 | 1 | 3 | Bit | 0x10 | - | Signal: Resetting the slow Switchgear Alarm
SG[1] | CES Disturbed | 178 | 1 | 3 | Bit | 0x40 | - | Signal: Command Execution Supervision: Switching Command unsuccessful. Switchgear in disturbed position.
SG[1] | CES Fiel Interl | 178 | 1 | 3 | Bit | 0x80 | - | Signal: Command Execution Supervision: Switching Command not executed because of field interlocking.
SG[1] | CES ON d OFF | 178 | 1 | 3 | Bit | 0x400 | - | Signal: Command Execution Supervision: On Command during a pending OFF Command.
SG[1] | CES SwitchDir | 178 | 1 | 3 | Bit | 0x800 | - | Signal: Command Execution Supervision respectively Switching Direction Control: This signal becomes true, if a switch command is issued even though the switchgear is already in the requested position. Example: A switchgear that is already OFF should be switched OFF again (doubly). The same applies to CLOSE commands.
SG[1] | CES SG not ready | 178 | 1 | 3 | Bit | 0x1000 | - | Signal: Command Execution Supervision: Switchgear not ready
SG[1] | CES SyncTimeout | 178 | 1 | 3 | Bit | 0x2000 | - | Signal: Command Execution Supervision: Switching Command not executed. No Synchronization signal while t-sync was running.
SG[1] | CES succesf | 178 | 1 | 3 | Bit | 0x4000 | - | Signal: Command Execution Supervision: Switching command executed successfully.
SG[1] | Prot ON | 178 | 1 | 3 | Bit | 0x8000 | - | Signal: ON Command issued by the Prot module
SG[1] | Pos Disturb | 179 | 1 | 3 | Bit | 0x1 | - | Signal: Circuit Breaker Disturbed - Undefined Breaker Position. The Position Indicators contradict themselves. After expiring of a supervision timer this signal becomes true.
SG[1] | t-Dwell | 179 | 1 | 3 | Bit | 0x2 | - | Signal: Dwell time
SG[1] | Pos Indeterm | 179 | 1 | 3 | Bit | 0x4 | - | Signal: Circuit Breaker is in Indeterminate Position
SG[1] | Pos OFF | 179 | 1 | 3 | Bit | 0x8 | - | Signal: Circuit Breaker is in OFF-Position
SG[1] | Pos ON | 179 | 1 | 3 | Bit | 0x10 | - | Signal: Circuit Breaker is in ON-Position
SG[1] | Ready | 179 | 1 | 3 | Bit | 0x20 | - | Signal: Circuit breaker is ready for operation.
SG[1] | Pos not ON | 179 | 1 | 3 | Bit | 0x40 | - | Signal: Pos not ON
SG[1] | SI SingleContactInd | 179 | 1 | 3 | Bit | 0x80 | - | Signal: The Position of the Switchgear is detected by one auxiliary contact (pole) only. Thus indeterminate and disturbed Positions cannot be detected.
SG[1] | Position Ind manipul | 179 | 1 | 3 | Bit | 0x100 | - | Signal: Position Indicators faked
SG[1] | OFF incl TripCmd | 179 | 1 | 3 | Bit | 0x200 | - | Signal: The OFF Command includes the OFF Command issued by the Protection module.
SG[1] | ON incl Prot ON | 179 | 1 | 3 | Bit | 0x400 | - | Signal: The ON Command includes the ON Command issued by the Protection module.
SG[1] | CES Fail TripCmd | 179 | 1 | 3 | Bit | 0x800 | - | Signal: Command Execution Supervision: Command execution failed because trip command is pending.
SG[1] | Interl OFF | 179 | 1 | 3 | Bit | 0x1000 | - | Signal: One or more IL_Off inputs are active.
SG[1] | Interl ON | 179 | 1 | 3 | Bit | 0x2000 | - | Signal: One or more IL_On inputs are active.
SG[1] | Isum Intr trip | 195 | 1 | 3 | Bit | 0x10 | - | Signal: Maximum permissible Summation of the interrupting (tripping) currents exceeded in at least one phase.
SG[1] | Isum Intr trip: IL1 | 195 | 1 | 3 | Bit | 0x20 | - | Signal: Maximum permissible Summation of the interrupting (tripping) currents exceeded: IL1
SG[1] | Isum Intr trip: IL2 | 195 | 1 | 3 | Bit | 0x40 | - | Signal: Maximum permissible Summation of the interrupting (tripping) currents exceeded: IL2
SG[1] | Isum Intr trip: IL3 | 195 | 1 | 3 | Bit | 0x80 | - | Signal: Maximum permissible Summation of the interrupting (tripping) currents exceeded: IL3
SG[1] | Operations Alarm | 195 | 1 | 3 | Bit | 0x100 | - | Signal: Too many Operations. (The operations counter »TripCmd Cr« has exceeded the limit set at »Operations Alarm«.)
SG[1] | WearLevel Alarm | 195 | 1 | 3 | Bit | 0x200 | - | Signal: Threshold for the Alarm
SG[1] | WearLevel Lockout | 195 | 1 | 3 | Bit | 0x400 | - | Signal: Threshold for the Lockout Level
SG[1] | Isum Intr ph Alm | 195 | 1 | 3 | Bit | 0x800 | - | Signal: Alarm, the per hour Sum (Limit) of interrupting currents has been exceeded.
SG[1] | Removed-I | 256 | 1 | 3 | Bit | 0x1 | - | State of the module input: The withdrawable circuit breaker is Removed
SG[1] | CES SG removed | 256 | 1 | 3 | Bit | 0x2 | - | Signal: Command Execution Supervision: Switching Command unsuccessful, Switchgear removed.
SG[1] | Removed | 256 | 1 | 3 | Bit | 0x4 | - | Signal: The withdrawable circuit breaker is Removed
SOTF | ExBlo1-I | 65 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking
SOTF | ExBlo2-I | 65 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking
SOTF | Ext SOTF-I | 65 | 1 | 3 | Bit | 0x4 | - | Module input state: External Switch Onto Fault Alarm
SOTF | Ex rev Interl-I | 65 | 1 | 3 | Bit | 0x8 | - | Module input state: External reverse interlocking
SOTF | Active | 65 | 1 | 3 | Bit | 0x10 | - | Signal: active
SOTF | ExBlo | 65 | 1 | 3 | Bit | 0x20 | - | Signal: External Blocking
SOTF | Ex rev Interl | 65 | 1 | 3 | Bit | 0x40 | - | Signal: External reverse Interlocking
SOTF | AR Blo | 65 | 1 | 3 | Bit | 0x400 | - | Signal: Blocked by AR
SOTF | enabled | 65 | 1 | 3 | Bit | 0x800 | - | Signal: Switch Onto Fault enabled. This Signal can be used to modify Overcurrent Protection Settings.
SOTF | I< | 65 | 1 | 3 | Bit | 0x2000 | - | Signal: No Load Current.
SSV | System Error | 273 | 1 | 3 | Bit | 0x1 | - | Signal: Device Failure
SSV | New error (*) | 273 | 1 | 3 | Bit | 0x8 | - | Signal: A new error message has been issued.
SSV | New warning (*) | 273 | 1 | 3 | Bit | 0x10 | - | Signal: A new warning message has been issued.
SSV | Active | 273 | 1 | 3 | Bit | 0x20 | - | Signal: active
Sgen | ExBlo1-I | 1012 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
Sgen | Ex ForcePost-I | 1012 | 1 | 3 | Bit | 0x2 | - | State of the module input:Force Post state. Abort simulation.
Sgen | Running | 1012 | 1 | 3 | Bit | 0x10 | - | Signal: Measuring value simulation is running
Sgen | State | 1012 | 1 | 3 | Bit | 0xe0 | - | Signal: Wave generation states: 0=Off, 1=PreFault, 2=Fault, 3=PostFault, 4=InitReset
Sgen | Ex Start Simulation-I | 1012 | 1 | 3 | Bit | 0x100 | - | State of the module input:External Start of Fault Simulation (Using the test parameters)
Sgen | ExBlo2-I | 1012 | 1 | 3 | Bit | 0x200 | - | Module input state: External blocking2
Sgen | Manual Start | 1012 | 1 | 3 | Bit | 0x400 | - | Fault Simulation has been started manually.
Sgen | Manual Stop | 1012 | 1 | 3 | Bit | 0x800 | - | Fault Simulation has been stopped manually.
Sgen | Started | 1012 | 1 | 3 | Bit | 0x1000 | - | Fault Simulation has been started
Sgen | Stopped | 1012 | 1 | 3 | Bit | 0x2000 | - | Fault Simulation has been stopped
Sys | Maint Mode Active | 154 | 1 | 3 | Bit | 0x1 | - | Signal: Arc Flash Reduction Maintenance Active
Sys | MaintMode Manually | 154 | 1 | 3 | Bit | 0x2 | - | Signal: Arc Flash Reduction Maintenance Manual Mode
Sys | Maint Mode DI | 154 | 1 | 3 | Bit | 0x4 | - | Signal: Arc Flash Reduction Maintenance Digital Input Mode
Sys | Maint Mode SCADA | 154 | 1 | 3 | Bit | 0x8 | - | Signal: Arc Flash Reduction Maintenance SCADA Mode
Sys | Maint Mode Inactive | 154 | 1 | 3 | Bit | 0x10 | - | Signal: Arc Flash Reduction Maintenance Inactive
Sys | Maint Mode-I | 154 | 1 | 3 | Bit | 0x20 | - | Module Input State: Arc Flash Reduction Maintenance Switch
Sys | Setting Lock-I | 154 | 1 | 3 | Bit | 0x40 | - | State of the module input: No parameters can be changed as long as this input is true. The parameter settings are locked.
Sys | SNTP active | 154 | 1 | 3 | Bit | 0x80 | - | Signal: If there is no valid SNTP signal for 120 sec, SNTP is regarded as inactive.
Sys | Setting Lock Bypass | 154 | 1 | 3 | Bit | 0x100 | - | Signal: Short-period unlock of the Setting Lock
SysA | ExBlo-I | 173 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking
SysA | ExBlo | 173 | 1 | 3 | Bit | 0x2 | - | Signal: External Blocking
SysA | Alm Current avg (Demd) | 173 | 1 | 3 | Bit | 0x4 | - | Signal: Alarm: Averaged demand current exceeded
SysA | Active | 173 | 1 | 3 | Bit | 0x8 | - | Signal: active
SysA | Alarm I THD | 173 | 1 | 3 | Bit | 0x10 | - | Signal: Alarm Total Harmonic Distortion Current
SysA | Trip Current avg (Demd) (*) | 173 | 1 | 3 | Bit | 0x1000 | - | Signal: Trip: Averaged demand current exceeded
SysA | Trip I THD (*) | 173 | 1 | 3 | Bit | 0x2000 | - | Signal: Trip Total Harmonic Distortion Current
TCS | ExBlo1-I | 150 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
TCS | ExBlo2-I | 150 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
TCS | Active | 150 | 1 | 3 | Bit | 0x4 | - | Signal: active
TCS | ExBlo | 150 | 1 | 3 | Bit | 0x8 | - | Signal: External Blocking
TCS | Alarm | 150 | 1 | 3 | Bit | 0x10 | - | Signal: Alarm Trip Circuit Supervision
TCS | Not Possible | 150 | 1 | 3 | Bit | 0x20 | - | Not possible because no state indicator assigned to the breaker.
TCS | Aux ON-I | 150 | 1 | 3 | Bit | 0x100 | - | Module Input State: Position indicator/check-back signal of the CB (52a)
TCS | Aux OFF-I | 150 | 1 | 3 | Bit | 0x200 | - | Module input state: Position indicator/check-back signal of the CB (52b)
ThR | ExBlo1-I | 19 | 1 | 3 | Bit | 0x1 | - | Module input state: External blocking1
ThR | ExBlo2-I | 19 | 1 | 3 | Bit | 0x2 | - | Module input state: External blocking2
ThR | ExBlo TripCmd-I | 19 | 1 | 3 | Bit | 0x4 | - | Module input state: External Blocking of the Trip Command
ThR | Active | 19 | 1 | 3 | Bit | 0x8 | - | Signal: active
ThR | ExBlo | 19 | 1 | 3 | Bit | 0x10 | - | Signal: External Blocking
ThR | Blo TripCmd | 19 | 1 | 3 | Bit | 0x20 | - | Signal: Trip Command blocked
ThR | ExBlo TripCmd | 19 | 1 | 3 | Bit | 0x40 | - | Signal: External Blocking of the Trip Command
ThR | Alarm | 19 | 1 | 3 | Bit | 0x80 | - | Signal: Alarm Thermal Overload
ThR | Trip (*) | 19 | 1 | 3 | Bit | 0x100 | - | Signal: Trip
ThR | TripCmd (*) | 19 | 1 | 3 | Bit | 0x200 | - | Signal: Trip Command
TimeSync | synchronized | 54 | 1 | 3 | Bit | 0x1 | - | Clock is synchronized.

## Adjust
Module | Subgroup names | Start register | No. of Registers | Function code | Format | Bit Mask / (Bit position) | Unit | Description
Date and Time | y | 32500 | 6 | 3 16 | Short | Word 0 | - | year
Date and Time | m | 32500 | 6 | 3 16 | Short | Word 1 | - | month
Date and Time | d | 32500 | 6 | 3 16 | Short | Word 2 | - | days
Date and Time | h | 32500 | 6 | 3 16 | Short | Word 3 | - | hours
Date and Time | min | 32500 | 6 | 3 16 | Short | Word 4 | - | minute
Date and Time | ms | 32500 | 6 | 3 16 | Short | Word 5 | - | milliseconds
Fault rec | RecordNo | 50000 | 9 | 3 16 | Short | Word 0 | - | Record Number
Fault rec | Trip Cause | 50000 | 9 | 3 16 | Short | Word 1 | - | Code for the trip cause. In case of several simultaneous trip causes the primary cause is selected. If there is another trip later then the new trip cause overwrites the previous one. The codes for the trip cause are documented in the SCADA documentation.
Fault rec | Pickup Cause | 50000 | 9 | 3 16 | Short | Word 2 | - | Code for last PickUp cause corresponds to fault record: See scada doc for correlation between pickup reason and code
Fault rec | Fault No. | 50000 | 9 | 3 16 | Short | Word 3 | - | Fault number
Fault rec | No. of Grid Faults | 50000 | 9 | 3 16 | Short | Word 4 | - | Number of grid faults: This is a counter for all faults (i.e. General Alarms »Prot . Alarm«), but except faults during a running cycle of the Automatic Reclosure module (signal »AR . running«). (Remark: The »Fault No.« counts every new fault independent of AR cycles. This means that for protective devices without AR module these two counters are equivalent.)
Fault rec | Time stamp: | 50000 | 9 | 3 16 | long long | Word 5- Word 8 | - | Timestamp in milliseconds since 1970

## Command
Module | Subgroup names | Start register | No. of Registers | Function code | Format | Bit Mask / (Bit position) | Unit | Description
Acknowledge | LEDs | 22000 | 1 | 5 | 0xFF00 | Word 0 | - | LEDs
Acknowledge | Binary Outputs | 22001 | 1 | 5 | 0xFF00 | Word 0 | - | Binary Outputs
Acknowledge | Scada | 22002 | 1 | 5 | 0xFF00 | Word 0 | - | Scada
Acknowledge | Device | 22003 | 1 | 5 | 0xFF00 | Word 0 | - | Device
Acknowledge | Ack TripCmd | 22005 | 1 | 5 | 0xFF00 | Word 0 | - | Signal: Acknowledge Trip Command
Reset | Modbus diagnosis counter | 22006 | 1 | 5 | 0xFF00 | Word 0 | - | Modbus diagnosis counter
Scada Cmd | Assbl Scada Cmd 1 | 22020 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 2 | 22021 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 3 | 22022 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 4 | 22023 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 5 | 22024 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 6 | 22025 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 7 | 22026 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 8 | 22027 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 9 | 22028 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 10 | 22029 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 11 | 22030 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 12 | 22031 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 13 | 22032 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 14 | 22033 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 15 | 22034 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Scada Cmd | Assbl Scada Cmd 16 | 22035 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Assignable Scada Command
Fault rec | Res all rec | 22040 | 1 | 5 | 0xFF00 | Word 0 | - | Reset all records
PSet-Switch | Scada PS1 | 22050 | 1 | 5 | 0xFF00 | Word 0 | - | Scada Setting Group1
PSet-Switch | Scada PS2 | 22051 | 1 | 5 | 0xFF00 | Word 0 | - | Scada Setting Group2
PSet-Switch | Scada PS3 | 22052 | 1 | 5 | 0xFF00 | Word 0 | - | Scada Setting Group3
PSet-Switch | Scada PS4 | 22053 | 1 | 5 | 0xFF00 | Word 0 | - | Scada Setting Group4
Maint Mode | Maint Mode SCADA | 22054 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Signal: Arc Flash Reduction Maintenance SCADA Mode
SG | SG ControlCmd1 | 22100 | 1 | 5 | 0xFF00=On ~~ 0x0000=Off | Word 0 | - | Control Command Switchgear

## Measure
Module | Subgroup names | Start register | No. of Registers | Function code | Format | Bit Mask / (Bit position) | Unit | Description
AR | Total number Cr | 20164 | 2 | 4 | Float IEE754 | Word 0 | - | Total number of all executed Automatic Reclosures Attempts
AR | Cr failed | 20166 | 2 | 4 | Float IEE754 | Word 0 | - | Total number of unsuccessfully executed automatic reclosure attempts
AR | Cr successfl | 20168 | 2 | 4 | Float IEE754 | Word 0 | - | Total number of successfully executed Automatic Reclosures
AR | Cr Service Alarm1 | 20170 | 2 | 4 | Float IEE754 | Word 0 | - | Remaining numbers of ARs until Service Alarm 1
AR | Cr Service Alarm2 | 20172 | 2 | 4 | Float IEE754 | Word 0 | - | Remaining numbers of ARs until Service Alarm 2
AR | AR Shot No. | 20188 | 2 | 4 | Float IEE754 | Word 0 | - | Counter - Auto Reclosure Attempts
AR | Max Shots / h Cr | 20374 | 2 | 4 | Float IEE754 | Word 0 | - | Counter for the maximum allowed shots per hour.
CT | IL1 | 20100 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (fundamental)
CT | IL2 | 20102 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (fundamental)
CT | IL3 | 20104 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (fundamental)
CT | IG meas | 20106 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (measured): IG (fundamental)
CT | I0 | 20114 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): Zero current (fundamental)
CT | I1 | 20116 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): Positive phase sequence current (fundamental)
CT | I2 | 20118 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): Unbalanced load current (fundamental)
CT | IL1 H2 | 20120 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value: 2nd harmonic/1st harmonic of IL1
CT | IL2 H2 | 20122 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value: 2nd harmonic/1st harmonic of IL2
CT | IL3 H2 | 20124 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value: 2nd harmonic/1st harmonic of IL3
CT | IG calc | 20160 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): IG (fundamental)
CT | phi IG calc | 20200 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IG calc\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude.
CT | phi IG meas | 20202 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IG meas\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude.
CT | phi IL1 | 20204 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IL1\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude.
CT | phi IL2 | 20206 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IL2\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude.
CT | phi IL3 | 20208 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IL3\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude.
CT | IL1 THD | 20210 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): IL1 Total Harmonic Current
CT | IL2 THD | 20212 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): IL2 Total Harmonic Current
CT | IL3 THD | 20214 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): IL3 Total Harmonic Current
CT | %IL1 THD | 20216 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value (calculated): IL1 Total Harmonic Distortion
CT | %IL2 THD | 20218 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value (calculated): IL2 Total Harmonic Distortion
CT | %IL3 THD | 20220 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value (calculated): IL3 Total Harmonic Distortion
CT | IL1 RMS | 20316 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (RMS)
CT | IL2 RMS | 20318 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (RMS)
CT | IL3 RMS | 20320 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (RMS)
CT | IG meas RMS | 20322 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (measured): IG (RMS)
CT | IG calc RMS | 20324 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): IG (RMS)
CT | %(I2/I1) | 20376 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value (calculated): I2/I1, phase sequence will be taken into account automatically.
CT | phi I0 | 20378 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle Zero Sequence System\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude.
CT | phi I1 | 20380 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Positive Sequence System\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude.
CT | phi I2 | 20382 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured Value (calculated): Angle of Negative Sequence System\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude.
CT | I1 max | 21074 | 2 | 4 | Float IEE754 | Word 0 | A | Maximum value positive phase sequence current (fundamental)
CT | I1 min | 21076 | 2 | 4 | Float IEE754 | Word 0 | A | Minimum value positive phase sequence current (fundamental)
CT | I2 max | 21080 | 2 | 4 | Float IEE754 | Word 0 | A | Maximum value negative sequence current (fundamental)
CT | I2 min | 21082 | 2 | 4 | Float IEE754 | Word 0 | A | Minimum value unbalanced load current (fundamental)
CT | IL1 avg RMS | 21130 | 2 | 4 | Float IEE754 | Word 0 | A | IL1 average value (RMS)
CT | IL2 avg RMS | 21132 | 2 | 4 | Float IEE754 | Word 0 | A | IL2 average value (RMS)
CT | IL3 avg RMS | 21134 | 2 | 4 | Float IEE754 | Word 0 | A | IL3 average value (RMS)
CT | IL1 max RMS | 21136 | 2 | 4 | Float IEE754 | Word 0 | A | IL1 maximum value (RMS)
CT | IL2 max RMS | 21138 | 2 | 4 | Float IEE754 | Word 0 | A | IL2 maximum value (RMS)
CT | IL3 max RMS | 21140 | 2 | 4 | Float IEE754 | Word 0 | A | IL3 maximum value (RMS)
CT | IL1 min RMS | 21142 | 2 | 4 | Float IEE754 | Word 0 | A | IL1 minimum value (RMS)
CT | IL2 min RMS | 21144 | 2 | 4 | Float IEE754 | Word 0 | A | IL2 minimum value (RMS)
CT | IL3 min RMS | 21146 | 2 | 4 | Float IEE754 | Word 0 | A | IL3 minimum value (RMS)
CT | IL1 H2 max | 21228 | 2 | 4 | Float IEE754 | Word 0 | % | Maximum ratio of 2nd harmonic over fundamental of IL1
CT | IL1 H2 min | 21230 | 2 | 4 | Float IEE754 | Word 0 | % | Minimum ratio of 2nd harmonic over fundamental of IL1
CT | IL2 H2 max | 21234 | 2 | 4 | Float IEE754 | Word 0 | % | Maximum ratio of 2nd harmonic over fundamental of IL2
CT | IL2 H2 min | 21236 | 2 | 4 | Float IEE754 | Word 0 | % | Minimum ratio of 2nd harmonic over fundamental of IL2
CT | IL3 H2 max | 21240 | 2 | 4 | Float IEE754 | Word 0 | % | Maximum ratio of 2nd harmonic over fundamental of IL3
CT | IL3 H2 min | 21242 | 2 | 4 | Float IEE754 | Word 0 | % | Minimum ratio of 2nd harmonic/1st harmonic minimum value of IL3
CT | IG calc max RMS | 21456 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated):IG maximum value (RMS)
CT | IG calc min RMS | 21458 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated):IG minimum value (RMS)
CT | IG meas max RMS | 21462 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: IG maximum value (RMS)
CT | IG meas min RMS | 21464 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: IG minimum value (RMS)
CT | %(I2/I1) max | 21468 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value (calculated): I2/I1 maximum value, phase sequence will be taken into account automatically
CT | %(I2/I1) min | 21470 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value (calculated): I2/I1 minimum value, phase sequence will be taken into account automatically
CT | IL1 Peak (Demand) | 21784 | 2 | 4 | Float IEE754 | Word 0 | A | IL1 Peak value, RMS value
CT | IL2 Peak (Demand) | 21786 | 2 | 4 | Float IEE754 | Word 0 | A | IL2 Peak value, RMS value
CT | IL3 Peak (Demand) | 21788 | 2 | 4 | Float IEE754 | Word 0 | A | IL3 Peak value, RMS value
CT - fault value | IL1 | 50100 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (fundamental) , as stored in the Fault Recorder
CT - fault value | IL2 | 50102 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (fundamental) , as stored in the Fault Recorder
CT - fault value | IL3 | 50104 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (fundamental) , as stored in the Fault Recorder
CT - fault value | IG meas | 50106 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (measured): IG (fundamental) , as stored in the Fault Recorder
CT - fault value | I0 | 50114 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): Zero current (fundamental) , as stored in the Fault Recorder
CT - fault value | I1 | 50116 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): Positive phase sequence current (fundamental) , as stored in the Fault Recorder
CT - fault value | I2 | 50118 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): Unbalanced load current (fundamental) , as stored in the Fault Recorder
CT - fault value | IL1 H2 | 50120 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value: 2nd harmonic/1st harmonic of IL1 , as stored in the Fault Recorder
CT - fault value | IL2 H2 | 50122 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value: 2nd harmonic/1st harmonic of IL2 , as stored in the Fault Recorder
CT - fault value | IL3 H2 | 50124 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value: 2nd harmonic/1st harmonic of IL3 , as stored in the Fault Recorder
CT - fault value | IG calc | 50160 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): IG (fundamental) , as stored in the Fault Recorder
CT - fault value | phi IG calc | 50200 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IG calc\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder
CT - fault value | phi IG meas | 50202 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IG meas\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder
CT - fault value | phi IL1 | 50204 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IL1\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder
CT - fault value | phi IL2 | 50206 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IL2\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder
CT - fault value | phi IL3 | 50208 | 2 | 4 | Float IEE754 | Word 0 | ° | Measured value (calculated): Angle of Phasor IL3\nReference phasor is required to calculate the angle. This is the first measured voltage (or current) channel with sufficiently high amplitude. , as stored in the Fault Recorder
CT - fault value | IL1 RMS | 50316 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (RMS) , as stored in the Fault Recorder
CT - fault value | IL2 RMS | 50318 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (RMS) , as stored in the Fault Recorder
CT - fault value | IL3 RMS | 50320 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value: Phase current (RMS) , as stored in the Fault Recorder
CT - fault value | IG meas RMS | 50322 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (measured): IG (RMS) , as stored in the Fault Recorder
CT - fault value | IG calc RMS | 50324 | 2 | 4 | Float IEE754 | Word 0 | A | Measured value (calculated): IG (RMS) , as stored in the Fault Recorder
CT - fault value | %(I2/I1) | 50376 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value (calculated): I2/I1, phase sequence will be taken into account automatically. , as stored in the Fault Recorder
Date and Time | y | 20000 | 6 | 4 | Short | Word 0 | - | year
Date and Time | m | 20000 | 6 | 4 | Short | Word 1 | - | month
Date and Time | d | 20000 | 6 | 4 | Short | Word 2 | - | days
Date and Time | h | 20000 | 6 | 4 | Short | Word 3 | - | hours
Date and Time | min | 20000 | 6 | 4 | Short | Word 4 | - | minute
Date and Time | ms | 20000 | 6 | 4 | Short | Word 5 | - | milliseconds
IRIG-B | Edges | 20298 | 2 | 4 | Float IEE754 | Word 0 | - | Edges: Total number of rising and falling edges. This signal indicates if a signal is available at the IRIG-B input.
IRIG-B | NoOfFrameErrors | 20300 | 2 | 4 | Float IEE754 | Word 0 | - | Total Number of Frame Errors. Physically corrupted Frame.
IRIG-B | NoOfFramesOK | 20302 | 2 | 4 | Float IEE754 | Word 0 | - | Total Number valid Frames.
Modbus | Mapped Meas 1 | 23000 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 2 | 23002 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 3 | 23004 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 4 | 23006 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 5 | 23008 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 6 | 23010 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 7 | 23012 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 8 | 23014 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 9 | 23016 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 10 | 23018 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 11 | 23020 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 12 | 23022 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 13 | 23024 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 14 | 23026 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 15 | 23028 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
Modbus | Mapped Meas 16 | 23030 | 2 | 4 | Float IEE754 | Word 0 | - | Mapped Measured Values. They can be used to provide measured values to the Modbus Master.
SG[1] | Sum trip IL1 | 20800 | 2 | 4 | Float IEE754 | Word 0 | A | Summation of the tripping currents phase
SG[1] | Sum trip IL2 | 20802 | 2 | 4 | Float IEE754 | Word 0 | A | Summation of the tripping currents phase
SG[1] | Sum trip IL3 | 20804 | 2 | 4 | Float IEE754 | Word 0 | A | Summation of the tripping currents phase
SG[1] | Isum Intr per hour | 20806 | 2 | 4 | Float IEE754 | Word 0 | kA | Sum per hour of interrupting currents.
SG[1] | Bkr Wear Level | 20808 | 2 | 4 | Float IEE754 | Word 0 | % | Wear level of the circuit breaker. (100% means that the circuit breaker has to be maintained.)
SG[1] | TripCmd Cr | 20810 | 2 | 4 | Float IEE754 | Word 0 | - | Counter: Total number of trips of the switchgear.
ThR | Thermal Level | 20110 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value: Ongoing thermal level
ThR | Time To Trip | 20112 | 2 | 4 | Float IEE754 | Word 0 | s | Measured value (calculated/measured): Remaining time until the thermal overload module will trip
ThR | Thermal Cap max | 21086 | 2 | 4 | Float IEE754 | Word 0 | % | Thermal Capacity maximum value
ThR - fault value | Thermal Level | 50110 | 2 | 4 | Float IEE754 | Word 0 | % | Measured value: Ongoing thermal level , as stored in the Fault Recorder
ThR - fault value | Time To Trip | 50112 | 2 | 4 | Float IEE754 | Word 0 | s | Measured value (calculated/measured): Remaining time until the thermal overload module will trip , as stored in the Fault Recorder
Values | Build | 20008 | 2 | 4 | Float IEE754 | Word 0 | - | Build Number
Values | Operating hours Cr | 20010 | 2 | 4 | Float IEE754 | Word 0 | h | Operating hours counter of the protective device

## causeOfTrip
COT modules | COT Code | COT description
| 1 | NORM
IG[1] | 1201
IG[2] | 1202
IG[3] | 1203
IG[4] | 1204
ExP[1] | 1306
ExP[2] | 1307
ExP[3] | 1308
ExP[4] | 1309
I2>[1] | 2901
I2>[2] | 2902
I[1] | 3201
I[2] | 3202
I[3] | 3203
I[4] | 3204
I[5] | 3205
I[6] | 3206
ThR | 3801