{"text_format":"2","workbook":"xlsx","n_sheets":6,"sheets":["Version","FC1 (Statusinformationen)","FC3 (Statusinformationen)","FC4 (Messwerte)","FC5 (Einzelne Befehle)","Enum (Fehlerquellen)"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Version","index":0,"n_rows":4,"n_cols":2,"rows_kept":4,"cut":false,"hidden":false,"merged":[]}
["Name","Info"]
["Gerät","WIC1"]
["DM-Version","2.2.a"]
["Build","64196"]

{"sheet":"FC1 (Statusinformationen)","index":1,"n_rows":159,"n_cols":5,"rows_kept":159,"cut":false,"hidden":false,"merged":[]}
["Adresse","Informationsobjekt","Selbsthaltung","Filter","Beschreibung"]
["00000001","Schutz.Aktiv","nein","x","Meldung: aktiv"]
["00000002","Schutz.Alarm","nein","x","Meldung: General-Alarm"]
["00000003","Schutz.Anregung","nein","x","Meldung: General-Anregung"]
["00000004","Schutz.Auslösung","ja","x","Meldung: General-Auslösung"]
["00000005","Schutz.AuslBef","ja","x","Meldung: Auslösebefehl"]
["00000006","Schutz.Anregung IL1","nein","x","Meldung: General-Anregung auf Grund eines Fehlers in Phase L1"]
["00000007","Schutz.Anregung IL2","nein","x","Meldung: General-Anregung auf Grund eines Fehlers in Phase L2"]
["00000008","Schutz.Anregung IL3","nein","x","Meldung: General-Anregung auf Grund eines Fehlers in Phase L3"]
["00000009","Schutz.Anregung IE","nein","x","Meldung: General-Anregung auf Grund eines Erdstrom-Fehlers"]
["00000010","Schutz.Anregung I Ph","nein","x","Meldung: General-Anregung auf Grund eines Phasenstrom-Fehlers"]
["00000011","Schutz.Anregung Ext.","nein","x","Meldung: General-Anregung durch externes Auslöse-Signal"]
["00000012","Schutz.Auslösung IL1","ja","x","Meldung: General-Auslösung auf Grund eines Fehlers in Phase L1"]
["00000013","Schutz.Auslösung IL2","ja","x","Meldung: General-Auslösung auf Grund eines Fehlers in Phase L2"]
["00000014","Schutz.Auslösung IL3","ja","x","Meldung: General-Auslösung auf Grund eines Fehlers in Phase L3"]
["00000015","Schutz.Auslösung IE","ja","x","Meldung: General-Auslösung auf Grund eines Erdstrom-Fehlers"]
["00000016","Schutz.Auslösung IPh","ja","x","Meldung: General-Auslösung auf Grund eines Phasenstrom-Fehlers"]
["00000017","Schutz.Auslösung Ext.","ja","x","Meldung: General-Auslösung durch externes Auslöse-Signal"]
["00000018","Schutz.Pos EIN","nein","x","Meldung: Leistungsschalter ist in EIN-Position"]
["00000019","Schutz.Pos AUS","nein","x","Meldung: Leistungsschalter ist in AUS-Position"]
["00000020","Schutz.Syst.OK. & mit Hilfssp.","nein","x","Meldung: Das WIC1 ist gestartet und wird über eine externe Hilfsspannung versorgt und hat genug elektrische Energie für den Impulsausgang zur Auslösung geladen."]
["00000021","Schutz.DI 1","nein","x","Meldung: Digitaler Eingang"]
["00000022","Schutz.DI 2","nein","x","Meldung: Digitaler Eingang"]
["00000023","Schutz.ExBlo AuslBef-E","nein","x","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["00000024","Schutz.EIN Bef","nein","x","Meldung: Einschaltbefehl an das Schaltgerät"]
["00000025","I>.Aktiv","nein","x","Meldung: aktiv"]
["00000026","I>.Auslösung","ja","x","Meldung: Auslösung"]
["00000027","I>.Alarm","nein","x","Meldung: Alarm"]
["00000028","I>.Anregung","nein","x","Meldung: Anregung"]
["00000029","I>.Auslösung IL1","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L1"]
["00000030","I>.Auslösung IL2","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L2"]
["00000031","I>.Auslösung IL3","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L3"]
["00000032","I>.Alarm IL1","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L1"]
["00000033","I>.Alarm IL2","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L2"]
["00000034","I>.Alarm IL3","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L3"]
["00000035","I>.Anregung IL1","nein","x","Meldung: Anregung in Phase L1"]
["00000036","I>.Anregung IL2","nein","x","Meldung: Anregung in Phase L2"]
["00000037","I>.Anregung IL3","nein","x","Meldung: Anregung in Phase L3"]
["00000038","I>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000039","I>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000040","I>>.Aktiv","nein","x","Meldung: aktiv"]
["00000041","I>>.Auslösung","ja","x","Meldung: Auslösung"]
["00000042","I>>.Alarm","nein","x","Meldung: Alarm"]
["00000043","I>>.Anregung","nein","x","Meldung: Anregung"]
["00000044","I>>.Auslösung IL1","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L1"]
["00000045","I>>.Auslösung IL2","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L2"]
["00000046","I>>.Auslösung IL3","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L3"]
["00000047","I>>.Alarm IL1","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L1"]
["00000048","I>>.Alarm IL2","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L2"]
["00000049","I>>.Alarm IL3","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L3"]
["00000050","I>>.Anregung IL1","nein","x","Meldung: Anregung in Phase L1"]
["00000051","I>>.Anregung IL2","nein","x","Meldung: Anregung in Phase L2"]
["00000052","I>>.Anregung IL3","nein","x","Meldung: Anregung in Phase L3"]
["00000053","I>>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000054","I>>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000055","I>>>.Aktiv","nein","x","Meldung: aktiv"]
["00000056","I>>>.Auslösung","ja","x","Meldung: Auslösung"]
["00000057","I>>>.Alarm","nein","x","Meldung: Alarm"]
["00000058","I>>>.Anregung","nein","x","Meldung: Anregung"]
["00000059","I>>>.Auslösung IL1","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L1"]
["00000060","I>>>.Auslösung IL2","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L2"]
["00000061","I>>>.Auslösung IL3","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L3"]
["00000062","I>>>.Alarm IL1","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L1"]
["00000063","I>>>.Alarm IL2","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L2"]
["00000064","I>>>.Alarm IL3","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L3"]
["00000065","I>>>.Anregung IL1","nein","x","Meldung: Anregung in Phase L1"]
["00000066","I>>>.Anregung IL2","nein","x","Meldung: Anregung in Phase L2"]
["00000067","I>>>.Anregung IL3","nein","x","Meldung: Anregung in Phase L3"]
["00000068","I>>>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000069","I>>>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000070","IE>.Aktiv","nein","x","Meldung: aktiv"]
["00000071","IE>.Auslösung","ja","x","Meldung: Auslösung"]
["00000072","IE>.Alarm","nein","x","Meldung: Alarm"]
["00000073","IE>.Anregung","nein","x","Meldung: Anregung"]
["00000074","IE>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000075","IE>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000076","IE>>.Aktiv","nein","x","Meldung: aktiv"]
["00000077","IE>>.Auslösung","ja","x","Meldung: Auslösung"]
["00000078","IE>>.Alarm","nein","x","Meldung: Alarm"]
["00000079","IE>>.Anregung","nein","x","Meldung: Anregung"]
["00000080","IE>>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000081","IE>>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000082","I2/I1>.Aktiv","nein","x","Meldung: aktiv"]
["00000083","I2/I1>.Auslösung","ja","x","Meldung: Auslösung"]
["00000084","I2/I1>.Alarm","nein","x","Meldung: Alarm"]
["00000085","I2/I1>.Anregung","nein","x","Meldung: Anregung"]
["00000086","I2/I1>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000087","I2/I1>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000088","I2>.Aktiv","nein","x","Meldung: aktiv"]
["00000089","I2>.Auslösung","ja","x","Meldung: Auslösung"]
["00000090","I2>.Alarm","nein","x","Meldung: Alarm"]
["00000091","I2>.Anregung","nein","x","Meldung: Anregung"]
["00000092","I2>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000093","I2>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000094","ThA.Aktiv","nein","x","Meldung: aktiv"]
["00000095","ThA.Auslösung","ja","x","Meldung: Auslösung"]
["00000096","ThA.Alarm","nein","x","Meldung: Alarm"]
["00000097","ThA.Anregung","nein","x","Meldung: Anregung"]
["00000098","ThA.Vorwarnung","nein","x","Meldung: Der eingestellte Θ-Schwellwert wurde überschritten."]
["00000099","ThA.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000100","Ipeak>.Aktiv","nein","x","Meldung: aktiv"]
["00000101","Ipeak>.Auslösung","ja","x","Meldung: Auslösung"]
["00000102","Ipeak>.Alarm","nein","x","Meldung: Alarm"]
["00000103","Ipeak>.Anregung","nein","x","Meldung: Anregung"]
["00000104","Ipeak>.Auslösung IL1","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L1"]
["00000105","Ipeak>.Auslösung IL2","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L2"]
["00000106","Ipeak>.Auslösung IL3","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L3"]
["00000107","Ipeak>.Alarm IL1","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L1"]
["00000108","Ipeak>.Alarm IL2","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L2"]
["00000109","Ipeak>.Alarm IL3","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L3"]
["00000110","Ipeak>.Anregung IL1","nein","x","Meldung: Anregung in Phase L1"]
["00000111","Ipeak>.Anregung IL2","nein","x","Meldung: Anregung in Phase L2"]
["00000112","Ipeak>.Anregung IL3","nein","x","Meldung: Anregung in Phase L3"]
["00000113","Ipeak>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000114","FAS.Aktiv","nein","x","Meldung: aktiv"]
["00000115","FAS.Auslösung","ja","x","Meldung: Auslösung"]
["00000116","FAS.Alarm","nein","x","Meldung: Alarm"]
["00000117","FAS.Anregung","nein","x","Meldung: Anregung"]
["00000118","FAS.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000119","FAS.Trigger-E","nein","x","Zustand des Moduleingangs: Auswahl desjenigen Anregesignals, das das FAS-Modul anstößt. Wenn dieses Anregesignal gegeben wird, regt (auch) das FAS-Modul an."]
["00000120","ExS[1].Aktiv","nein","x","Meldung: aktiv"]
["00000121","ExS[1].Auslösung","ja","x","Meldung: Auslösung"]
["00000122","ExS[1].Alarm","nein","x","Alarm"]
["00000123","ExS[1].Anregung","nein","x","Meldung: Anregung"]
["00000124","ExS[1].ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000125","ExS[1].Trigger-Signal-E","nein","x","Zustand des Moduleingangs: Externes Trigger-Signal"]
["00000126","ExS[2].Aktiv","nein","x","Meldung: aktiv"]
["00000127","ExS[2].Auslösung","ja","x","Meldung: Auslösung"]
["00000128","ExS[2].Alarm","nein","x","Alarm"]
["00000129","ExS[2].Anregung","nein","x","Meldung: Anregung"]
["00000130","ExS[2].ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000131","ExS[2].Trigger-Signal-E","nein","x","Zustand des Moduleingangs: Externes Trigger-Signal"]
["00000132","ExS[2].Bedingung-E","nein","x","Zustand des Moduleingangs: Bedingung für Externen Schutz"]
["00000133","AKÜ.Aktiv","nein","x","Meldung: aktiv"]
["00000134","AKÜ.Alarm","nein","x","Meldung: Alarm"]
["00000135","AKÜ.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000136","IH2.Aktiv","nein","x","Meldung: aktiv"]
["00000137","IH2.Block. L1","nein","x","Meldung: Inrush-Blockade von Phase L1 des Phasen-Überstromschutzes"]
["00000138","IH2.Block. L2","nein","x","Meldung: Inrush-Blockade von Phase L2 des Phasen-Überstromschutzes"]
["00000139","IH2.Block. L3","nein","x","Meldung: Inrush-Blockade von Phase L3 des Phasen-Überstromschutzes"]
["00000140","IH2.Block. Erde","nein","x","Meldung: Inrush-Blockade des Erd-Überstromschutzes und in mindestens einer Phase des Phasen-Überstromschutzes."]
["00000141","IH2.Block. 3-ph","nein","x","Meldung: 3-phasige Inrush-Blockade: Es wurde in (mindestens) einer Phase ein Inrush erkannt und deswegen alle drei Phasen blockiert."]
["00000142","IH2.Imax überschritten","nein","x","Meldung: Der Inrush-Grenzwert wurde überschritten, sodass die Inrush-Blockade verhindert wurde."]
["00000143","IH2.tmax abgelaufen","nein","x","Meldung: Die (phasen-selektive) Maximaldauer der Inrush-Blockade ist erreicht, sodass die Inrush-Blockade beendet wurde."]
["00000144","Life Load.Aktiv","nein","x","Meldung: aktiv"]
["00000145","Life Load.Alarm","nein","x","Meldung: Alarm"]
["00000146","Life Load.Assign_1_","nein","x","Assignement 1 example_"]
["00000147","LSV.Aktiv","nein","x","Meldung: aktiv"]
["00000148","LSV.Alarm","nein","x","Meldung: Alarm"]
["00000149","LSV.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000150","SGW.Aktiv","nein","x","Meldung: aktiv"]
["00000151","SGW.Alarm","nein","x","Meldung: Alarm: Die maximale Anzahl Ausschaltvorgänge oder die maximal mögliche Summe der abgeschalteten Ströme wurde überschritten."]
["00000152","SGW.Alm(max.Sum.Ausl)","nein","x","Meldung: Alarm: Die maximale Anzahl Ausschaltvorgänge wurde überschritten."]
["00000153","SGW.Alm(max.Sum.Iaus)","nein","x","Meldung: Alarm: Die maximal mögliche Summe der abgeschalteten Ströme wurde überschritten."]
["00000154","SGW.Alm (LS-Verschl.)","nein","x","Meldung: Alarm: Der maximal mögliche Abnutzungsgrad des Leistungsschalters wurde überschritten."]
["00000155","KLA.Aktiv","nein","x","Meldung: aktiv"]
["00000156","KLA.angestoßen","nein","x","Meldung: Die KLA-Stabilisierung wurde angestoßen."]
["00000157","KLA.stab.","nein","x","Meldung: Die KLA-Stabilisierung ist aktiv."]
["00000158","KLA.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]

{"sheet":"FC3 (Statusinformationen)","index":2,"n_rows":159,"n_cols":7,"rows_kept":159,"cut":false,"hidden":false,"merged":[]}
["Adresse","Bit-Länge","Bit-Position","Informationsobjekt","Selbsthaltung","Filter","Beschreibung"]
["00000001","1","00","Schutz.Aktiv","nein","x","Meldung: aktiv"]
["00000001","1","01","Schutz.Alarm","nein","x","Meldung: General-Alarm"]
["00000001","1","02","Schutz.Anregung","nein","x","Meldung: General-Anregung"]
["00000001","1","03","Schutz.Auslösung","ja","x","Meldung: General-Auslösung"]
["00000001","1","04","Schutz.AuslBef","ja","x","Meldung: Auslösebefehl"]
["00000001","1","05","Schutz.Anregung IL1","nein","x","Meldung: General-Anregung auf Grund eines Fehlers in Phase L1"]
["00000001","1","06","Schutz.Anregung IL2","nein","x","Meldung: General-Anregung auf Grund eines Fehlers in Phase L2"]
["00000001","1","07","Schutz.Anregung IL3","nein","x","Meldung: General-Anregung auf Grund eines Fehlers in Phase L3"]
["00000001","1","08","Schutz.Anregung IE","nein","x","Meldung: General-Anregung auf Grund eines Erdstrom-Fehlers"]
["00000001","1","09","Schutz.Anregung I Ph","nein","x","Meldung: General-Anregung auf Grund eines Phasenstrom-Fehlers"]
["00000001","1","10","Schutz.Anregung Ext.","nein","x","Meldung: General-Anregung durch externes Auslöse-Signal"]
["00000001","1","11","Schutz.Auslösung IL1","ja","x","Meldung: General-Auslösung auf Grund eines Fehlers in Phase L1"]
["00000001","1","12","Schutz.Auslösung IL2","ja","x","Meldung: General-Auslösung auf Grund eines Fehlers in Phase L2"]
["00000001","1","13","Schutz.Auslösung IL3","ja","x","Meldung: General-Auslösung auf Grund eines Fehlers in Phase L3"]
["00000001","1","14","Schutz.Auslösung IE","ja","x","Meldung: General-Auslösung auf Grund eines Erdstrom-Fehlers"]
["00000001","1","15","Schutz.Auslösung IPh","ja","x","Meldung: General-Auslösung auf Grund eines Phasenstrom-Fehlers"]
["00000002","1","00","Schutz.Auslösung Ext.","ja","x","Meldung: General-Auslösung durch externes Auslöse-Signal"]
["00000002","1","01","Schutz.Pos EIN","nein","x","Meldung: Leistungsschalter ist in EIN-Position"]
["00000002","1","02","Schutz.Pos AUS","nein","x","Meldung: Leistungsschalter ist in AUS-Position"]
["00000002","1","03","Schutz.Syst.OK. & mit Hilfssp.","nein","x","Meldung: Das WIC1 ist gestartet und wird über eine externe Hilfsspannung versorgt und hat genug elektrische Energie für den Impulsausgang zur Auslösung geladen."]
["00000002","1","04","Schutz.DI 1","nein","x","Meldung: Digitaler Eingang"]
["00000002","1","05","Schutz.DI 2","nein","x","Meldung: Digitaler Eingang"]
["00000002","1","06","Schutz.ExBlo AuslBef-E","nein","x","Zustand des Moduleingangs: Externe Blockade des Auslösebefehls"]
["00000002","1","07","Schutz.EIN Bef","nein","x","Meldung: Einschaltbefehl an das Schaltgerät"]
["00000003","1","00","I>.Aktiv","nein","x","Meldung: aktiv"]
["00000003","1","01","I>.Auslösung","ja","x","Meldung: Auslösung"]
["00000003","1","02","I>.Alarm","nein","x","Meldung: Alarm"]
["00000003","1","03","I>.Anregung","nein","x","Meldung: Anregung"]
["00000003","1","04","I>.Auslösung IL1","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L1"]
["00000003","1","05","I>.Auslösung IL2","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L2"]
["00000003","1","06","I>.Auslösung IL3","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L3"]
["00000003","1","07","I>.Alarm IL1","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L1"]
["00000003","1","08","I>.Alarm IL2","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L2"]
["00000003","1","09","I>.Alarm IL3","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L3"]
["00000003","1","10","I>.Anregung IL1","nein","x","Meldung: Anregung in Phase L1"]
["00000003","1","11","I>.Anregung IL2","nein","x","Meldung: Anregung in Phase L2"]
["00000003","1","12","I>.Anregung IL3","nein","x","Meldung: Anregung in Phase L3"]
["00000003","1","13","I>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000003","1","14","I>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000004","1","00","I>>.Aktiv","nein","x","Meldung: aktiv"]
["00000004","1","01","I>>.Auslösung","ja","x","Meldung: Auslösung"]
["00000004","1","02","I>>.Alarm","nein","x","Meldung: Alarm"]
["00000004","1","03","I>>.Anregung","nein","x","Meldung: Anregung"]
["00000004","1","04","I>>.Auslösung IL1","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L1"]
["00000004","1","05","I>>.Auslösung IL2","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L2"]
["00000004","1","06","I>>.Auslösung IL3","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L3"]
["00000004","1","07","I>>.Alarm IL1","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L1"]
["00000004","1","08","I>>.Alarm IL2","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L2"]
["00000004","1","09","I>>.Alarm IL3","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L3"]
["00000004","1","10","I>>.Anregung IL1","nein","x","Meldung: Anregung in Phase L1"]
["00000004","1","11","I>>.Anregung IL2","nein","x","Meldung: Anregung in Phase L2"]
["00000004","1","12","I>>.Anregung IL3","nein","x","Meldung: Anregung in Phase L3"]
["00000004","1","13","I>>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000004","1","14","I>>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000005","1","00","I>>>.Aktiv","nein","x","Meldung: aktiv"]
["00000005","1","01","I>>>.Auslösung","ja","x","Meldung: Auslösung"]
["00000005","1","02","I>>>.Alarm","nein","x","Meldung: Alarm"]
["00000005","1","03","I>>>.Anregung","nein","x","Meldung: Anregung"]
["00000005","1","04","I>>>.Auslösung IL1","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L1"]
["00000005","1","05","I>>>.Auslösung IL2","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L2"]
["00000005","1","06","I>>>.Auslösung IL3","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L3"]
["00000005","1","07","I>>>.Alarm IL1","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L1"]
["00000005","1","08","I>>>.Alarm IL2","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L2"]
["00000005","1","09","I>>>.Alarm IL3","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L3"]
["00000005","1","10","I>>>.Anregung IL1","nein","x","Meldung: Anregung in Phase L1"]
["00000005","1","11","I>>>.Anregung IL2","nein","x","Meldung: Anregung in Phase L2"]
["00000005","1","12","I>>>.Anregung IL3","nein","x","Meldung: Anregung in Phase L3"]
["00000005","1","13","I>>>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000005","1","14","I>>>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000006","1","00","IE>.Aktiv","nein","x","Meldung: aktiv"]
["00000006","1","01","IE>.Auslösung","ja","x","Meldung: Auslösung"]
["00000006","1","02","IE>.Alarm","nein","x","Meldung: Alarm"]
["00000006","1","03","IE>.Anregung","nein","x","Meldung: Anregung"]
["00000006","1","04","IE>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000006","1","05","IE>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000007","1","00","IE>>.Aktiv","nein","x","Meldung: aktiv"]
["00000007","1","01","IE>>.Auslösung","ja","x","Meldung: Auslösung"]
["00000007","1","02","IE>>.Alarm","nein","x","Meldung: Alarm"]
["00000007","1","03","IE>>.Anregung","nein","x","Meldung: Anregung"]
["00000007","1","04","IE>>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000007","1","05","IE>>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000008","1","00","I2/I1>.Aktiv","nein","x","Meldung: aktiv"]
["00000008","1","01","I2/I1>.Auslösung","ja","x","Meldung: Auslösung"]
["00000008","1","02","I2/I1>.Alarm","nein","x","Meldung: Alarm"]
["00000008","1","03","I2/I1>.Anregung","nein","x","Meldung: Anregung"]
["00000008","1","04","I2/I1>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000008","1","05","I2/I1>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000009","1","00","I2>.Aktiv","nein","x","Meldung: aktiv"]
["00000009","1","01","I2>.Auslösung","ja","x","Meldung: Auslösung"]
["00000009","1","02","I2>.Alarm","nein","x","Meldung: Alarm"]
["00000009","1","03","I2>.Anregung","nein","x","Meldung: Anregung"]
["00000009","1","04","I2>.IH2 Blo","nein","x","Meldung: Blockade des Auslösebefehls durch einen Inrush"]
["00000009","1","05","I2>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000010","1","00","ThA.Aktiv","nein","x","Meldung: aktiv"]
["00000010","1","01","ThA.Auslösung","ja","x","Meldung: Auslösung"]
["00000010","1","02","ThA.Alarm","nein","x","Meldung: Alarm"]
["00000010","1","03","ThA.Anregung","nein","x","Meldung: Anregung"]
["00000010","1","04","ThA.Vorwarnung","nein","x","Meldung: Der eingestellte Θ-Schwellwert wurde überschritten."]
["00000010","1","05","ThA.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000011","1","00","Ipeak>.Aktiv","nein","x","Meldung: aktiv"]
["00000011","1","01","Ipeak>.Auslösung","ja","x","Meldung: Auslösung"]
["00000011","1","02","Ipeak>.Alarm","nein","x","Meldung: Alarm"]
["00000011","1","03","Ipeak>.Anregung","nein","x","Meldung: Anregung"]
["00000011","1","05","Ipeak>.Auslösung IL1","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L1"]
["00000011","1","06","Ipeak>.Auslösung IL2","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L2"]
["00000011","1","07","Ipeak>.Auslösung IL3","ja","x","Meldung: Auslösung auf Grund eines Fehlers in Phase L3"]
["00000011","1","08","Ipeak>.Alarm IL1","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L1"]
["00000011","1","09","Ipeak>.Alarm IL2","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L2"]
["00000011","1","10","Ipeak>.Alarm IL3","nein","x","Meldung: Alarm auf Grund eines Fehlers in Phase L3"]
["00000011","1","11","Ipeak>.Anregung IL1","nein","x","Meldung: Anregung in Phase L1"]
["00000011","1","12","Ipeak>.Anregung IL2","nein","x","Meldung: Anregung in Phase L2"]
["00000011","1","13","Ipeak>.Anregung IL3","nein","x","Meldung: Anregung in Phase L3"]
["00000011","1","14","Ipeak>.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000012","1","00","FAS.Aktiv","nein","x","Meldung: aktiv"]
["00000012","1","01","FAS.Auslösung","ja","x","Meldung: Auslösung"]
["00000012","1","02","FAS.Alarm","nein","x","Meldung: Alarm"]
["00000012","1","03","FAS.Anregung","nein","x","Meldung: Anregung"]
["00000012","1","04","FAS.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000012","1","05","FAS.Trigger-E","nein","x","Zustand des Moduleingangs: Auswahl desjenigen Anregesignals, das das FAS-Modul anstößt. Wenn dieses Anregesignal gegeben wird, regt (auch) das FAS-Modul an."]
["00000013","1","00","ExS[1].Aktiv","nein","x","Meldung: aktiv"]
["00000013","1","01","ExS[1].Auslösung","ja","x","Meldung: Auslösung"]
["00000013","1","02","ExS[1].Alarm","nein","x","Alarm"]
["00000013","1","03","ExS[1].Anregung","nein","x","Meldung: Anregung"]
["00000013","1","04","ExS[1].ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000013","1","05","ExS[1].Trigger-Signal-E","nein","x","Zustand des Moduleingangs: Externes Trigger-Signal"]
["00000014","1","00","ExS[2].Aktiv","nein","x","Meldung: aktiv"]
["00000014","1","01","ExS[2].Auslösung","ja","x","Meldung: Auslösung"]
["00000014","1","02","ExS[2].Alarm","nein","x","Alarm"]
["00000014","1","03","ExS[2].Anregung","nein","x","Meldung: Anregung"]
["00000014","1","04","ExS[2].ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000014","1","05","ExS[2].Trigger-Signal-E","nein","x","Zustand des Moduleingangs: Externes Trigger-Signal"]
["00000014","1","06","ExS[2].Bedingung-E","nein","x","Zustand des Moduleingangs: Bedingung für Externen Schutz"]
["00000015","1","00","AKÜ.Aktiv","nein","x","Meldung: aktiv"]
["00000015","1","01","AKÜ.Alarm","nein","x","Meldung: Alarm"]
["00000015","1","02","AKÜ.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000016","1","00","IH2.Aktiv","nein","x","Meldung: aktiv"]
["00000016","1","01","IH2.Block. L1","nein","x","Meldung: Inrush-Blockade von Phase L1 des Phasen-Überstromschutzes"]
["00000016","1","02","IH2.Block. L2","nein","x","Meldung: Inrush-Blockade von Phase L2 des Phasen-Überstromschutzes"]
["00000016","1","03","IH2.Block. L3","nein","x","Meldung: Inrush-Blockade von Phase L3 des Phasen-Überstromschutzes"]
["00000016","1","04","IH2.Block. Erde","nein","x","Meldung: Inrush-Blockade des Erd-Überstromschutzes und in mindestens einer Phase des Phasen-Überstromschutzes."]
["00000016","1","05","IH2.Block. 3-ph","nein","x","Meldung: 3-phasige Inrush-Blockade: Es wurde in (mindestens) einer Phase ein Inrush erkannt und deswegen alle drei Phasen blockiert."]
["00000016","1","06","IH2.Imax überschritten","nein","x","Meldung: Der Inrush-Grenzwert wurde überschritten, sodass die Inrush-Blockade verhindert wurde."]
["00000016","1","07","IH2.tmax abgelaufen","nein","x","Meldung: Die (phasen-selektive) Maximaldauer der Inrush-Blockade ist erreicht, sodass die Inrush-Blockade beendet wurde."]
["00000017","1","00","Life Load.Aktiv","nein","x","Meldung: aktiv"]
["00000017","1","01","Life Load.Alarm","nein","x","Meldung: Alarm"]
["00000017","1","02","Life Load.Assign_1_","nein","x","Assignement 1 example_"]
["00000018","1","00","LSV.Aktiv","nein","x","Meldung: aktiv"]
["00000018","1","01","LSV.Alarm","nein","x","Meldung: Alarm"]
["00000018","1","02","LSV.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]
["00000019","1","00","SGW.Aktiv","nein","x","Meldung: aktiv"]
["00000019","1","01","SGW.Alarm","nein","x","Meldung: Alarm: Die maximale Anzahl Ausschaltvorgänge oder die maximal mögliche Summe der abgeschalteten Ströme wurde überschritten."]
["00000019","1","02","SGW.Alm(max.Sum.Ausl)","nein","x","Meldung: Alarm: Die maximale Anzahl Ausschaltvorgänge wurde überschritten."]
["00000019","1","03","SGW.Alm(max.Sum.Iaus)","nein","x","Meldung: Alarm: Die maximal mögliche Summe der abgeschalteten Ströme wurde überschritten."]
["00000019","1","04","SGW.Alm (LS-Verschl.)","nein","x","Meldung: Alarm: Der maximal mögliche Abnutzungsgrad des Leistungsschalters wurde überschritten."]
["00000020","1","00","KLA.Aktiv","nein","x","Meldung: aktiv"]
["00000020","1","01","KLA.angestoßen","nein","x","Meldung: Die KLA-Stabilisierung wurde angestoßen."]
["00000020","1","02","KLA.stab.","nein","x","Meldung: Die KLA-Stabilisierung ist aktiv."]
["00000020","1","03","KLA.ExBlo-E","nein","x","Zustand des Moduleingangs: Externe Blockade"]

{"sheet":"FC4 (Messwerte)","index":3,"n_rows":82,"n_cols":10,"rows_kept":82,"cut":false,"hidden":false,"merged":[]}
["Adresse","Wort-Länge","Informationsobjekt","Format","Einheit","Faktor","Skalierung","Art des Werts","Filter","Beschreibung"]
["00001000","2","StW.IL1 ","Float","A","1.0","Primär","Messwert","x","Messwert: Phasenstrom (Grundwelle)"]
["00001002","2","StW.IL2 ","Float","A","1.0","Primär","Messwert","x","Messwert: Phasenstrom (Grundwelle)"]
["00001004","2","StW.IL3 ","Float","A","1.0","Primär","Messwert","x","Messwert: Phasenstrom (Grundwelle)"]
["00001006","2","StW.IE gem ","Float","A","1.0","Primär","Messwert","x","Messwert (gemessen): IE (Grundwelle)"]
["00001008","2","StW.IE err ","Float","A","1.0","Primär","Messwert","x","Messwert (errechnet): IE (Grundwelle) \nBei zu kleinen Phasenströmen ist der ermittelte Wert unzuverlässig bzw. ungültig. Dann wird als Wert „-0.0“ angezeigt."]
["00001010","2","StW.phi IL1","Float","°","1.0",".","Messwert","x","Messwert (errechnet): Phasenlage Stromzeiger IL1 \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00001012","2","StW.phi IL2","Float","°","1.0",".","Messwert","x","Messwert (errechnet): Phasenlage Stromzeiger IL2 \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00001014","2","StW.phi IL3","Float","°","1.0",".","Messwert","x","Messwert (errechnet): Phasenlage Stromzeiger IL3 \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00001016","2","StW.phi IE gem","Float","°","1.0",".","Messwert","x","Messwert (errechnet): Phasenlage Stromzeiger IE gem \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00001020","2","StW.phi IE err","Float","°","1.0",".","Messwert","x","Messwert (errechnet): Phasenlage Stromzeiger IE err \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00001022","2","StW.IL1 H2 ","Float","%","1.0",".","Messwert","x","Messwert: 2. Harmonische/Grundwelle von IL1"]
["00001024","2","StW.IL2 H2 ","Float","%","1.0",".","Messwert","x","Messwert: 2. Harmonische/Grundwelle von IL2"]
["00001026","2","StW.IL3 H2 ","Float","%","1.0",".","Messwert","x","Messwert: 2. Harmonische/Grundwelle von IL3"]
["00001028","2","StW.I0 ","Float","A","1.0","Primär","Messwert","x","Messwert (berechnet): Nullstrom (Grundwelle)"]
["00001030","2","StW.I1 ","Float","A","1.0","Primär","Messwert","x","Messwert (berechnet): Strom Mitsystem (Grundwelle)"]
["00001032","2","StW.I2 ","Float","A","1.0","Primär","Messwert","x","Messwert (berechnet): Strom Gegensystem (Grundwelle)"]
["00001034","2","StW.%(I2/I1)","Float","%","1.0",".","Messwert","x","Messwert (errechnet): I2/I1, Drehfeldrichtung wird automatisch berücksichtigt."]
["00001036","2","StW.IL1 RMS","Float","A","1.0","Primär","Messwert","x","Messwert: Phasenstrom (RMS)"]
["00001038","2","StW.IL2 RMS","Float","A","1.0","Primär","Messwert","x","Messwert: Phasenstrom (RMS)"]
["00001040","2","StW.IL3 RMS","Float","A","1.0","Primär","Messwert","x","Messwert: Phasenstrom (RMS)"]
["00001042","2","StW.IE gem RMS","Float","A","1.0","Primär","Messwert","x","Messwert (gemessen): IE (RMS)"]
["00001044","2","StW.IE err RMS","Float","A","1.0","Primär","Messwert","x","Messwert (errechnet): IE (RMS) \nBei zu kleinen Phasenströmen ist der ermittelte Wert unzuverlässig bzw. ungültig. Dann wird als Wert „-0.0“ angezeigt."]
["00001046","2","StW.%IL1 THD","Float","%","1.0",".","Messwert","x","Messwert (errechnet): IL1 Total Harmonic Distortion"]
["00001048","2","StW.%IL2 THD","Float","%","1.0",".","Messwert","x","Messwert (errechnet): IL2 Total Harmonic Distortion"]
["00001050","2","StW.%IL3 THD","Float","%","1.0",".","Messwert","x","Messwert (errechnet): IL3 Total Harmonic Distortion"]
["00001052","2","ThA.Therm. Niv.","Float","%","1.0",".","Messwert","x","Messwert: Aktuelles Thermisches Niveau"]
["00001054","2","Schleppzeiger.Imax","Float","A","1.0","Primär","Messwert","x","Maximalwert des Phasenstrommittels »Iavg« seit dem letzten Reset"]
["00001056","2","Schleppzeiger.Iavg","Float","A","1.0","Primär","Messwert","x","Maximalwert des Phasenstroms, gemittelt über das eingestellte Zeitfenster \nSolange der Mittelwert von »Iavg« noch nicht aussagekräftig ist, weil die Berechnung noch läuft, wird als Wert „-0.0“ angezeigt. (Erst nachdem das eingestellte Zeitfenster abgelaufen ist, wird ein gültiger Wert angezeigt.)"]
["00001058","2","Life Load.< 0,4 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001060","2","Life Load.0,4 ... 0,5 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001062","2","Life Load.0,5 ... 0,6 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001064","2","Life Load.0,6 ... 0,7 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001066","2","Life Load.0,7 ... 0,8 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001068","2","Life Load.0,8 ... 0,9 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001070","2","Life Load.0,9 ... 1,0 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001072","2","Life Load.1,0 ... 1,1 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001074","2","Life Load.1,1 ... 1,2 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001076","2","Life Load.> 1,2 In","Float","d","1.0",".","Messwert","x","Anzahl der Betriebstage mit Stromwerten innerhalb dieses Bereiches"]
["00001078","2","Life Load.Zeit bis Alm.","Float","d","1.0",".","Messwert","x","Zeit (in Tagen), die noch verbleibt, bis ein Alarm-Signal gegeben wird, weil das Gerät für zu lange Zeit einem zu hohen Phasenstrom ausgesetzt war. (Die Zeit zählt rückwärts von dem unter »Zeitschwelle« eingestellten Wert bis 0 und lässt sich mit dem Direktkommando »Rst. Alarm« zurücksetzen.)"]
["00001080","2","Sys.Betr.stund.","Float","h","1.0",".","Messwert","x","Der Betriebsstundenzähler gibt an, wie lange das Schutzgerät seit dem letzen Reset in Betrieb ist."]
["00005000","9","Modbus.Fehlerrek","Enum (Fehlerquellen)",".",".",".",".","x","Der übermittelte Fehlereintrag enthält Auslöseursache und -zeit als eine kombinierte Struktur. Diese besteht aus folgenden Komponenten, geordnet von den Adressen „low“ nach „high“:\n- [word 0, short] Aufz. Nr.\n- [Word 1, short] Ausl.-Ursache\n- [Word 2, short] Alarm Ursache(*)\n- [Word 3, short] Störfall-Nr.\n- [Word 4, short] Netzstör-Nr.\n- [Word 5 ... Word 8, long long] (WIC liefert hier nur Nullen.)\n(*) Codierung der Auslöseursache. Bei mehreren gleichzeitigen Auslöseursachen wird die primäre Ursache ausgewählt. Im Falle einer weiteren, späteren Auslösung überschreibt die neue Ursache die vorherige. Die Codierungen der Auslöseursachen sind in der SCADA-Dokumentation aufgeführt."]
["00010000","2","Sys.Build","Uint32",".","1.0",".","Messwert","x","Build-Nummer"]
["00010002","8","Sys.DM-Version","ASCII String. 16 Bytes",".",".",".",".","x","Version des Gerätemodells"]
["00010010","8","Sys.SW-Version","ASCII String. 16 Bytes",".",".",".",".","x","Version der Geräte-Firmware"]
["00010018","8","Sys.CAT No.","ASCII String. 16 Bytes",".",".",".",".","x","»CAT No.«, Bestellschlüssel gemäß Geräte-Aufdruck."]
["00010026","8","Sys.REV.","ASCII String. 16 Bytes",".",".",".",".","x","Revision (gemäß Geräte-Aufdruck)."]
["00010034","8","Sys.S/N","ASCII String. 16 Bytes",".",".",".",".","x","Seriennummer des Gerätes."]
["00010100","2","Sys.Build","Uint32",".","1.0",".","Messwert","x","Build-Nummer"]
["00010102","8","Sys.DM-Version","ASCII String. 16 Bytes",".",".",".",".","x","Version des Gerätemodells"]
["00010110","8","Sys.SW-Version","ASCII String. 16 Bytes",".",".",".",".","x","Version der Geräte-Firmware"]
["00010118","8","Sys.CAT No.","ASCII String. 16 Bytes",".",".",".",".","x","»CAT No.«, Bestellschlüssel gemäß Geräte-Aufdruck."]
["00010126","8","Sys.REV.","ASCII String. 16 Bytes",".",".",".",".","x","Revision (gemäß Geräte-Aufdruck)."]
["00010134","8","Sys.S/N","ASCII String. 16 Bytes",".",".",".",".","x","Seriennummer des Gerätes."]
["00010200","2","TcpIp.Build","Uint32",".","1.0",".","Messwert","x","Build-Nummer"]
["00010202","8","TcpIp.SW-Version","ASCII String. 16 Bytes",".",".",".",".","x","Version der Geräte-Firmware"]
["00010210","8","TcpIp.Komm.typ","ASCII String. 16 Bytes",".",".",".",".","x","Bezeichnung des (integrierten) Hardware-Moduls für die Kommunikations-Schnittstelle"]
["00011000","2","StW.IL1 ","Float","A","1.0","Primär","Fehlerwert","x","Messwert: Phasenstrom (Grundwelle)"]
["00011002","2","StW.IL2 ","Float","A","1.0","Primär","Fehlerwert","x","Messwert: Phasenstrom (Grundwelle)"]
["00011004","2","StW.IL3 ","Float","A","1.0","Primär","Fehlerwert","x","Messwert: Phasenstrom (Grundwelle)"]
["00011006","2","StW.IE gem ","Float","A","1.0","Primär","Fehlerwert","x","Messwert (gemessen): IE (Grundwelle)"]
["00011008","2","StW.IE err ","Float","A","1.0","Primär","Fehlerwert","x","Messwert (errechnet): IE (Grundwelle) \nBei zu kleinen Phasenströmen ist der ermittelte Wert unzuverlässig bzw. ungültig. Dann wird als Wert „-0.0“ angezeigt."]
["00011010","2","StW.phi IL1","Float","°","1.0",".","Fehlerwert","x","Messwert (errechnet): Phasenlage Stromzeiger IL1 \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00011012","2","StW.phi IL2","Float","°","1.0",".","Fehlerwert","x","Messwert (errechnet): Phasenlage Stromzeiger IL2 \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00011014","2","StW.phi IL3","Float","°","1.0",".","Fehlerwert","x","Messwert (errechnet): Phasenlage Stromzeiger IL3 \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00011016","2","StW.phi IE gem","Float","°","1.0",".","Fehlerwert","x","Messwert (errechnet): Phasenlage Stromzeiger IE gem \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00011020","2","StW.phi IE err","Float","°","1.0",".","Fehlerwert","x","Messwert (errechnet): Phasenlage Stromzeiger IE err \nBei zu kleiner Amplitude ist der ermittelte Winkel unzuverlässig bzw. ungültig. Dann wird als Winkel „360°“ angezeigt."]
["00011022","2","StW.IL1 H2 ","Float","%","1.0",".","Fehlerwert","x","Messwert: 2. Harmonische/Grundwelle von IL1"]
["00011024","2","StW.IL2 H2 ","Float","%","1.0",".","Fehlerwert","x","Messwert: 2. Harmonische/Grundwelle von IL2"]
["00011026","2","StW.IL3 H2 ","Float","%","1.0",".","Fehlerwert","x","Messwert: 2. Harmonische/Grundwelle von IL3"]
["00011028","2","StW.I0 ","Float","A","1.0","Primär","Fehlerwert","x","Messwert (berechnet): Nullstrom (Grundwelle)"]
["00011030","2","StW.I1 ","Float","A","1.0","Primär","Fehlerwert","x","Messwert (berechnet): Strom Mitsystem (Grundwelle)"]
["00011032","2","StW.I2 ","Float","A","1.0","Primär","Fehlerwert","x","Messwert (berechnet): Strom Gegensystem (Grundwelle)"]
["00011034","2","StW.%(I2/I1)","Float","%","1.0",".","Fehlerwert","x","Messwert (errechnet): I2/I1, Drehfeldrichtung wird automatisch berücksichtigt."]
["00011036","2","StW.IL1 RMS","Float","A","1.0","Primär","Fehlerwert","x","Messwert: Phasenstrom (RMS)"]
["00011038","2","StW.IL2 RMS","Float","A","1.0","Primär","Fehlerwert","x","Messwert: Phasenstrom (RMS)"]
["00011040","2","StW.IL3 RMS","Float","A","1.0","Primär","Fehlerwert","x","Messwert: Phasenstrom (RMS)"]
["00011042","2","StW.IE gem RMS","Float","A","1.0","Primär","Fehlerwert","x","Messwert (gemessen): IE (RMS)"]
["00011044","2","StW.IE err RMS","Float","A","1.0","Primär","Fehlerwert","x","Messwert (errechnet): IE (RMS) \nBei zu kleinen Phasenströmen ist der ermittelte Wert unzuverlässig bzw. ungültig. Dann wird als Wert „-0.0“ angezeigt."]
["00011052","2","ThA.Therm. Niv.","Float","%","1.0",".","Fehlerwert","x","Messwert: Aktuelles Thermisches Niveau"]
[]
["Hinweis zu Primär: Damit Primärwerte korrekt übertragen werden, muss das Übersetzungsverhältnis richtig parametriert sein, ansonsten liefert die Abfrage dieser Werte eine Null zurück."]

{"sheet":"FC5 (Einzelne Befehle)","index":4,"n_rows":10,"n_cols":3,"rows_kept":10,"cut":false,"hidden":false,"merged":[]}
["Adresse","Informationsobjekt","Beschreibung"]
["00002000","Modbus.Leittechnik","Direktkommando zum Zurücksetzen aller Modbus-Selbsthaltungs Statusinformationen."]
["00002001","Modbus.Rst. Zähler","Direktkommando zum Zurücksetzen aller Modbus-Diagnosezähler"]
["00002002","Schutz.Rst. LEDs, FIs","Direkt-Kommando, um alle gehaltenen LEDs, alle DiggiMEC-Schauzeichen sowie eine eventuell auf dem DiggiMEC-Display angezeigte Info zur Fehler-/Auslösungsursache zurückzusetzen."]
["00002003","Schutz.Rst. Alm-/Fehlerrek.","Direkt-Kommando, um alle Einträge im Alarm-/Fehlerrekorder zu löschen."]
["00002004","ThA.Rst. Therm. Niv.","Rücksetzen des Thermischen Niveaus"]
["00002005","Sys.Rst. Err.-LED","Direkt-Kommando, um einen Gerätefehler zu quittieren. Dadurch wird auch die System-LED (READY/ERROR) zurückgesetzt."]
["00002006","SGW.Reset","Direktkommando zum Zurücksetzen der Abnutzungsgrades (des Leistungsschalters) und der Zähler (für die Anzahl Auslösebefehle und für die Summe der abgeschalteten Ströme)."]
["00002007","Schleppzeiger.Zurück","Direktkommando zum Rücksetzen des »Imax«-Schleppzeigers"]
["00002008","Life Load.Rst. Alarm","Direktkommando zum Rücksetzen des Alarm-Signals. Hierdurch wird auch die (rückwärts zählende) »Zeit bis Alarm« wieder auf den Einstellwert »Zeitschwelle« zurückgesetzt."]

{"sheet":"Enum (Fehlerquellen)","index":5,"n_rows":30,"n_cols":3,"rows_kept":30,"cut":false,"hidden":false,"merged":[]}
["Wert","Modul","Beschreibung"]
["1","Schutz","Schutz-Hauptmodul"]
["2","StW","Stromwandler"]
["5","DiggiMEC","DiggiMEC"]
["6","Sys","System"]
["7","Sgen","Sinusgenerator"]
["8","TcpIp","TcpIp"]
["10","IH2","Modul Inrush"]
["11","I>","Phasenstromschutz-Stufe"]
["12","I>>","Phasenstromschutz-Stufe"]
["13","I>>>","Phasenstromschutz-Stufe"]
["14","IE>","Erdstromschutz-Stufe"]
["15","IE>>","Erdstromschutz-Stufe"]
["16","Ipeak>","Spitzenstrom-Schutz"]
["17","I2/I1>","Schieflast-Schutz"]
["18","I2>","Gegensystemstrom-Schutz"]
["19","ThA","Thermisches Abbild-Modul"]
["20","FAS","Fehleraufschaltung - Modul"]
["21","KLA","Kalte Last Alarm - Modul"]
["22","ExS[1]","Externer Schutz - Modul"]
["23","ExS[2]","Externer Schutz - Modul"]
["30","AKÜ","Auslösekreis-Überwachung"]
["31","LSV","Leistungsschalterversagerschutz-Modul"]
["32","SGW","Schaltgerätewartung"]
["33","SBattÜ","Überwachung der Stationsbatterie"]
["58","Life Load","Laststrom-Histogramm"]
["59","Schleppzeiger","Statistik der Strommesswerte"]
["60","Modbus","Modbus"]
[]
["Hinweis: Nicht alle Module führen zu einer Störschreiberaufzeichnung."]