{"text_format":"2","workbook":"xlsx","n_sheets":6,"sheets":["Version","FC1 (State Information)","FC3 (State Information)","FC4 (Measurement Data)","FC5 (Single Commands)","Enum (Fault Reasons)"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Version","index":0,"n_rows":4,"n_cols":2,"rows_kept":4,"cut":false,"hidden":false,"merged":[]}
["Name","Info"]
["Device","WIC1"]
["DM version","2.2.a"]
["Build","64196"]

{"sheet":"FC1 (State Information)","index":1,"n_rows":159,"n_cols":5,"rows_kept":159,"cut":false,"hidden":false,"merged":[]}
["Address","Information Object","Latched","filter","Description"]
["00000001","Prot.Active","no","x","Signal: active"]
["00000002","Prot.Alarm","no","x","Signal: General Alarm"]
["00000003","Prot.Pickup","no","x","Signal: General Pickup"]
["00000004","Prot.Trip","yes","x","Signal: General Trip"]
["00000005","Prot.TripCmd","yes","x","Signal: Trip Command"]
["00000006","Prot.Pickup IA","no","x","Signal: General Pickup due to a fault in phase A"]
["00000007","Prot.Pickup IB","no","x","Signal: General Pickup due to a fault in phase B"]
["00000008","Prot.Pickup IC","no","x","Signal: General Pickup due to a fault in phase C"]
["00000009","Prot.Pickup IG","no","x","Signal: General Pickup due to a ground current fault"]
["00000010","Prot.Pickup I Ph","no","x","Signal: General Pickup due to a phase current fault"]
["00000011","Prot.Pickup Ext.","no","x","Signal: General Pickup due to an external signal"]
["00000012","Prot.Trip IA","yes","x","Signal: General Trip due to a fault in phase A"]
["00000013","Prot.Trip IB","yes","x","Signal: General Trip due to a fault in phase B"]
["00000014","Prot.Trip IC","yes","x","Signal: General Trip due to a fault in phase C"]
["00000015","Prot.Trip IG","yes","x","Signal: General Trip due to a ground current fault"]
["00000016","Prot.Trip IPh","yes","x","Signal: General Trip due to a phase current fault"]
["00000017","Prot.Trip Ext.","yes","x","Signal: General Trip due to an external signal"]
["00000018","Prot.Pos ON","no","x","Signal: Circuit Breaker is in ON-Position"]
["00000019","Prot.Pos OFF","no","x","Signal: Circuit Breaker is in OFF-Position"]
["00000020","Prot.Syst. OK. & Ext.Suppl.","no","x","Signal: The WIC1 is running and is supplied by external auxiliary power and has loaded sufficient electrical energy for triggering the trip impulse output."]
["00000021","Prot.DI 1","no","x","Signal: Digital Input"]
["00000022","Prot.DI 2","no","x","Signal: Digital Input"]
["00000023","Prot.ExBlo TripCmd-I","no","x","Module input state: External Blocking of the Trip Command"]
["00000024","Prot.ON Cmd","no","x","Signal: ON command issued to the breaker"]
["00000025","I>.Active","no","x","Signal: active"]
["00000026","I>.Trip","yes","x","Signal: Trip"]
["00000027","I>.Alarm","no","x","Signal: Alarm"]
["00000028","I>.Pickup","no","x","Signal: Pickup"]
["00000029","I>.Trip IA","yes","x","Signal: Trip due to a fault in phase A"]
["00000030","I>.Trip IB","yes","x","Signal: Trip due to a fault in phase B"]
["00000031","I>.Trip IC","yes","x","Signal: Trip due to a fault in phase C"]
["00000032","I>.Alarm IA","no","x","Signal: Alarm due to a fault in phase A"]
["00000033","I>.Alarm IB","no","x","Signal: Alarm due to a fault in phase B"]
["00000034","I>.Alarm IC","no","x","Signal: Alarm due to a fault in phase C"]
["00000035","I>.Pickup IA","no","x","Signal: Pickup in phase A"]
["00000036","I>.Pickup IB","no","x","Signal: Pickup in phase B"]
["00000037","I>.Pickup IC","no","x","Signal: Pickup in phase C"]
["00000038","I>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000039","I>.ExBlo-I","no","x","Module input state: External blocking"]
["00000040","I>>.Active","no","x","Signal: active"]
["00000041","I>>.Trip","yes","x","Signal: Trip"]
["00000042","I>>.Alarm","no","x","Signal: Alarm"]
["00000043","I>>.Pickup","no","x","Signal: Pickup"]
["00000044","I>>.Trip IA","yes","x","Signal: Trip due to a fault in phase A"]
["00000045","I>>.Trip IB","yes","x","Signal: Trip due to a fault in phase B"]
["00000046","I>>.Trip IC","yes","x","Signal: Trip due to a fault in phase C"]
["00000047","I>>.Alarm IA","no","x","Signal: Alarm due to a fault in phase A"]
["00000048","I>>.Alarm IB","no","x","Signal: Alarm due to a fault in phase B"]
["00000049","I>>.Alarm IC","no","x","Signal: Alarm due to a fault in phase C"]
["00000050","I>>.Pickup IA","no","x","Signal: Pickup in phase A"]
["00000051","I>>.Pickup IB","no","x","Signal: Pickup in phase B"]
["00000052","I>>.Pickup IC","no","x","Signal: Pickup in phase C"]
["00000053","I>>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000054","I>>.ExBlo-I","no","x","Module input state: External blocking"]
["00000055","I>>>.Active","no","x","Signal: active"]
["00000056","I>>>.Trip","yes","x","Signal: Trip"]
["00000057","I>>>.Alarm","no","x","Signal: Alarm"]
["00000058","I>>>.Pickup","no","x","Signal: Pickup"]
["00000059","I>>>.Trip IA","yes","x","Signal: Trip due to a fault in phase A"]
["00000060","I>>>.Trip IB","yes","x","Signal: Trip due to a fault in phase B"]
["00000061","I>>>.Trip IC","yes","x","Signal: Trip due to a fault in phase C"]
["00000062","I>>>.Alarm IA","no","x","Signal: Alarm due to a fault in phase A"]
["00000063","I>>>.Alarm IB","no","x","Signal: Alarm due to a fault in phase B"]
["00000064","I>>>.Alarm IC","no","x","Signal: Alarm due to a fault in phase C"]
["00000065","I>>>.Pickup IA","no","x","Signal: Pickup in phase A"]
["00000066","I>>>.Pickup IB","no","x","Signal: Pickup in phase B"]
["00000067","I>>>.Pickup IC","no","x","Signal: Pickup in phase C"]
["00000068","I>>>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000069","I>>>.ExBlo-I","no","x","Module input state: External blocking"]
["00000070","IG>.Active","no","x","Signal: active"]
["00000071","IG>.Trip","yes","x","Signal: Trip"]
["00000072","IG>.Alarm","no","x","Signal: Alarm"]
["00000073","IG>.Pickup","no","x","Signal: Pickup"]
["00000074","IG>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000075","IG>.ExBlo-I","no","x","Module input state: External blocking"]
["00000076","IG>>.Active","no","x","Signal: active"]
["00000077","IG>>.Trip","yes","x","Signal: Trip"]
["00000078","IG>>.Alarm","no","x","Signal: Alarm"]
["00000079","IG>>.Pickup","no","x","Signal: Pickup"]
["00000080","IG>>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000081","IG>>.ExBlo-I","no","x","Module input state: External blocking"]
["00000082","I2/I1>.Active","no","x","Signal: active"]
["00000083","I2/I1>.Trip","yes","x","Signal: Trip"]
["00000084","I2/I1>.Alarm","no","x","Signal: Alarm"]
["00000085","I2/I1>.Pickup","no","x","Signal: Pickup"]
["00000086","I2/I1>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000087","I2/I1>.ExBlo-I","no","x","Module input state: External blocking"]
["00000088","I2>.Active","no","x","Signal: active"]
["00000089","I2>.Trip","yes","x","Signal: Trip"]
["00000090","I2>.Alarm","no","x","Signal: Alarm"]
["00000091","I2>.Pickup","no","x","Signal: Pickup"]
["00000092","I2>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000093","I2>.ExBlo-I","no","x","Module input state: External blocking"]
["00000094","ThR.Active","no","x","Signal: active"]
["00000095","ThR.Trip","yes","x","Signal: Trip"]
["00000096","ThR.Alarm","no","x","Signal: Alarm"]
["00000097","ThR.Pickup","no","x","Signal: Pickup"]
["00000098","ThR.Pre-Alarm","no","x","Signal: The set value for the Θ Threshold has been exceeded."]
["00000099","ThR.ExBlo-I","no","x","Module input state: External blocking"]
["00000100","Ipeak>.Active","no","x","Signal: active"]
["00000101","Ipeak>.Trip","yes","x","Signal: Trip"]
["00000102","Ipeak>.Alarm","no","x","Signal: Alarm"]
["00000103","Ipeak>.Pickup","no","x","Signal: Pickup"]
["00000104","Ipeak>.Trip IA","yes","x","Signal: Trip due to a fault in phase A"]
["00000105","Ipeak>.Trip IB","yes","x","Signal: Trip due to a fault in phase B"]
["00000106","Ipeak>.Trip IC","yes","x","Signal: Trip due to a fault in phase C"]
["00000107","Ipeak>.Alarm IA","no","x","Signal: Alarm due to a fault in phase A"]
["00000108","Ipeak>.Alarm IB","no","x","Signal: Alarm due to a fault in phase B"]
["00000109","Ipeak>.Alarm IC","no","x","Signal: Alarm due to a fault in phase C"]
["00000110","Ipeak>.Pickup IA","no","x","Signal: Pickup in phase A"]
["00000111","Ipeak>.Pickup IB","no","x","Signal: Pickup in phase B"]
["00000112","Ipeak>.Pickup IC","no","x","Signal: Pickup in phase C"]
["00000113","Ipeak>.ExBlo-I","no","x","Module input state: External blocking"]
["00000114","SOTF.Active","no","x","Signal: active"]
["00000115","SOTF.Trip","yes","x","Signal: Trip"]
["00000116","SOTF.Alarm","no","x","Signal: Alarm"]
["00000117","SOTF.Pickup","no","x","Signal: Pickup"]
["00000118","SOTF.ExBlo-I","no","x","Module input state: External blocking"]
["00000119","SOTF.Trigger-I","no","x","State of the module input: Assign the type of pickup signal that triggers the SOTF module. If the assigned pickup signal is issued, the SOTF module itself picks up."]
["00000120","ExP[1].Active","no","x","Signal: active"]
["00000121","ExP[1].Trip","yes","x","Signal: Trip"]
["00000122","ExP[1].Alarm","no","x","Alarm"]
["00000123","ExP[1].Pickup","no","x","Signal: Pickup"]
["00000124","ExP[1].ExBlo-I","no","x","Module input state: External blocking"]
["00000125","ExP[1].Trigger Signal-I","no","x","State of the module input: External trigger signal"]
["00000126","ExP[2].Active","no","x","Signal: active"]
["00000127","ExP[2].Trip","yes","x","Signal: Trip"]
["00000128","ExP[2].Alarm","no","x","Alarm"]
["00000129","ExP[2].Pickup","no","x","Signal: Pickup"]
["00000130","ExP[2].ExBlo-I","no","x","Module input state: External blocking"]
["00000131","ExP[2].Trigger Signal-I","no","x","State of the module input: External trigger signal"]
["00000132","ExP[2].Condition-I","no","x","State of the module input: Condition for External Protection"]
["00000133","TCM.Active","no","x","Signal: active"]
["00000134","TCM.Alarm","no","x","Signal: Alarm"]
["00000135","TCM.ExBlo-I","no","x","Module input state: External blocking"]
["00000136","IH2.Active","no","x","Signal: active"]
["00000137","IH2.Block. A","no","x","Signal: Inrush blocking of phase A of the phase overcurrent protection"]
["00000138","IH2.Block. B","no","x","Signal: Inrush blocking of phase B of the phase overcurrent protection"]
["00000139","IH2.Block. C","no","x","Signal: Inrush blocking of phase C of the phase overcurrent protection"]
["00000140","IH2.Block. Ground","no","x","Signal: Inrush blocking of the ground (earth) overcurrent protection and min. 1 phase of the phase overcurrent protection."]
["00000141","IH2.Block. 3-ph","no","x","Signal: 3-phase Inrush blocking: An inrush has been detected in (at least) one phase, so that all three phases are blocked."]
["00000142","IH2.Imax exceeded","no","x","Signal: The Inrush limit value has been exceeded, so that the inrush blocking has been cancelled."]
["00000143","IH2.tmax elapsed","no","x","Signal: The (phase-selective) maximum duration of an inrush blocking has been reached, so that the inrush blocking has been stopped."]
["00000144","Life Load.Active","no","x","Signal: active"]
["00000145","Life Load.Alarm","no","x","Signal: Alarm"]
["00000146","Life Load.Assign_1_","no","x","Assignement 1 example_"]
["00000147","CBF.Active","no","x","Signal: active"]
["00000148","CBF.Alarm","no","x","Signal: Alarm"]
["00000149","CBF.ExBlo-I","no","x","Module input state: External blocking"]
["00000150","BkrWear.Active","no","x","Signal: active"]
["00000151","BkrWear.Alarm","no","x","Signal: Alarm: The maximum number of open commands or the maximum value for the sum of ruptured currents has been exceeded."]
["00000152","BkrWear.Alm(mx.Sum.Tr)","no","x","Signal: Alarm: The maximum number of open commands has been exceeded."]
["00000153","BkrWear.Alm(mx.Sum.Itrip)","no","x","Signal: Alarm: The maximum value for the sum of ruptured currents has been exceeded."]
["00000154","BkrWear.Alm (CB Wear Lev.)","no","x","Signal: Alarm: The maximum wear level of the circuit breaker has been exceeded."]
["00000155","CLPU.Active","no","x","Signal: active"]
["00000156","CLPU.detected","no","x","Signal: The CLPU stabilization has been triggered."]
["00000157","CLPU.stab.","no","x","Signal: The CLPU stabilization is active."]
["00000158","CLPU.ExBlo-I","no","x","Module input state: External blocking"]

{"sheet":"FC3 (State Information)","index":2,"n_rows":159,"n_cols":7,"rows_kept":159,"cut":false,"hidden":false,"merged":[]}
["Address","Bit size","Bit position","Information Object","Latched","filter","Description"]
["00000001","1","00","Prot.Active","no","x","Signal: active"]
["00000001","1","01","Prot.Alarm","no","x","Signal: General Alarm"]
["00000001","1","02","Prot.Pickup","no","x","Signal: General Pickup"]
["00000001","1","03","Prot.Trip","yes","x","Signal: General Trip"]
["00000001","1","04","Prot.TripCmd","yes","x","Signal: Trip Command"]
["00000001","1","05","Prot.Pickup IA","no","x","Signal: General Pickup due to a fault in phase A"]
["00000001","1","06","Prot.Pickup IB","no","x","Signal: General Pickup due to a fault in phase B"]
["00000001","1","07","Prot.Pickup IC","no","x","Signal: General Pickup due to a fault in phase C"]
["00000001","1","08","Prot.Pickup IG","no","x","Signal: General Pickup due to a ground current fault"]
["00000001","1","09","Prot.Pickup I Ph","no","x","Signal: General Pickup due to a phase current fault"]
["00000001","1","10","Prot.Pickup Ext.","no","x","Signal: General Pickup due to an external signal"]
["00000001","1","11","Prot.Trip IA","yes","x","Signal: General Trip due to a fault in phase A"]
["00000001","1","12","Prot.Trip IB","yes","x","Signal: General Trip due to a fault in phase B"]
["00000001","1","13","Prot.Trip IC","yes","x","Signal: General Trip due to a fault in phase C"]
["00000001","1","14","Prot.Trip IG","yes","x","Signal: General Trip due to a ground current fault"]
["00000001","1","15","Prot.Trip IPh","yes","x","Signal: General Trip due to a phase current fault"]
["00000002","1","00","Prot.Trip Ext.","yes","x","Signal: General Trip due to an external signal"]
["00000002","1","01","Prot.Pos ON","no","x","Signal: Circuit Breaker is in ON-Position"]
["00000002","1","02","Prot.Pos OFF","no","x","Signal: Circuit Breaker is in OFF-Position"]
["00000002","1","03","Prot.Syst. OK. & Ext.Suppl.","no","x","Signal: The WIC1 is running and is supplied by external auxiliary power and has loaded sufficient electrical energy for triggering the trip impulse output."]
["00000002","1","04","Prot.DI 1","no","x","Signal: Digital Input"]
["00000002","1","05","Prot.DI 2","no","x","Signal: Digital Input"]
["00000002","1","06","Prot.ExBlo TripCmd-I","no","x","Module input state: External Blocking of the Trip Command"]
["00000002","1","07","Prot.ON Cmd","no","x","Signal: ON command issued to the breaker"]
["00000003","1","00","I>.Active","no","x","Signal: active"]
["00000003","1","01","I>.Trip","yes","x","Signal: Trip"]
["00000003","1","02","I>.Alarm","no","x","Signal: Alarm"]
["00000003","1","03","I>.Pickup","no","x","Signal: Pickup"]
["00000003","1","04","I>.Trip IA","yes","x","Signal: Trip due to a fault in phase A"]
["00000003","1","05","I>.Trip IB","yes","x","Signal: Trip due to a fault in phase B"]
["00000003","1","06","I>.Trip IC","yes","x","Signal: Trip due to a fault in phase C"]
["00000003","1","07","I>.Alarm IA","no","x","Signal: Alarm due to a fault in phase A"]
["00000003","1","08","I>.Alarm IB","no","x","Signal: Alarm due to a fault in phase B"]
["00000003","1","09","I>.Alarm IC","no","x","Signal: Alarm due to a fault in phase C"]
["00000003","1","10","I>.Pickup IA","no","x","Signal: Pickup in phase A"]
["00000003","1","11","I>.Pickup IB","no","x","Signal: Pickup in phase B"]
["00000003","1","12","I>.Pickup IC","no","x","Signal: Pickup in phase C"]
["00000003","1","13","I>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000003","1","14","I>.ExBlo-I","no","x","Module input state: External blocking"]
["00000004","1","00","I>>.Active","no","x","Signal: active"]
["00000004","1","01","I>>.Trip","yes","x","Signal: Trip"]
["00000004","1","02","I>>.Alarm","no","x","Signal: Alarm"]
["00000004","1","03","I>>.Pickup","no","x","Signal: Pickup"]
["00000004","1","04","I>>.Trip IA","yes","x","Signal: Trip due to a fault in phase A"]
["00000004","1","05","I>>.Trip IB","yes","x","Signal: Trip due to a fault in phase B"]
["00000004","1","06","I>>.Trip IC","yes","x","Signal: Trip due to a fault in phase C"]
["00000004","1","07","I>>.Alarm IA","no","x","Signal: Alarm due to a fault in phase A"]
["00000004","1","08","I>>.Alarm IB","no","x","Signal: Alarm due to a fault in phase B"]
["00000004","1","09","I>>.Alarm IC","no","x","Signal: Alarm due to a fault in phase C"]
["00000004","1","10","I>>.Pickup IA","no","x","Signal: Pickup in phase A"]
["00000004","1","11","I>>.Pickup IB","no","x","Signal: Pickup in phase B"]
["00000004","1","12","I>>.Pickup IC","no","x","Signal: Pickup in phase C"]
["00000004","1","13","I>>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000004","1","14","I>>.ExBlo-I","no","x","Module input state: External blocking"]
["00000005","1","00","I>>>.Active","no","x","Signal: active"]
["00000005","1","01","I>>>.Trip","yes","x","Signal: Trip"]
["00000005","1","02","I>>>.Alarm","no","x","Signal: Alarm"]
["00000005","1","03","I>>>.Pickup","no","x","Signal: Pickup"]
["00000005","1","04","I>>>.Trip IA","yes","x","Signal: Trip due to a fault in phase A"]
["00000005","1","05","I>>>.Trip IB","yes","x","Signal: Trip due to a fault in phase B"]
["00000005","1","06","I>>>.Trip IC","yes","x","Signal: Trip due to a fault in phase C"]
["00000005","1","07","I>>>.Alarm IA","no","x","Signal: Alarm due to a fault in phase A"]
["00000005","1","08","I>>>.Alarm IB","no","x","Signal: Alarm due to a fault in phase B"]
["00000005","1","09","I>>>.Alarm IC","no","x","Signal: Alarm due to a fault in phase C"]
["00000005","1","10","I>>>.Pickup IA","no","x","Signal: Pickup in phase A"]
["00000005","1","11","I>>>.Pickup IB","no","x","Signal: Pickup in phase B"]
["00000005","1","12","I>>>.Pickup IC","no","x","Signal: Pickup in phase C"]
["00000005","1","13","I>>>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000005","1","14","I>>>.ExBlo-I","no","x","Module input state: External blocking"]
["00000006","1","00","IG>.Active","no","x","Signal: active"]
["00000006","1","01","IG>.Trip","yes","x","Signal: Trip"]
["00000006","1","02","IG>.Alarm","no","x","Signal: Alarm"]
["00000006","1","03","IG>.Pickup","no","x","Signal: Pickup"]
["00000006","1","04","IG>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000006","1","05","IG>.ExBlo-I","no","x","Module input state: External blocking"]
["00000007","1","00","IG>>.Active","no","x","Signal: active"]
["00000007","1","01","IG>>.Trip","yes","x","Signal: Trip"]
["00000007","1","02","IG>>.Alarm","no","x","Signal: Alarm"]
["00000007","1","03","IG>>.Pickup","no","x","Signal: Pickup"]
["00000007","1","04","IG>>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000007","1","05","IG>>.ExBlo-I","no","x","Module input state: External blocking"]
["00000008","1","00","I2/I1>.Active","no","x","Signal: active"]
["00000008","1","01","I2/I1>.Trip","yes","x","Signal: Trip"]
["00000008","1","02","I2/I1>.Alarm","no","x","Signal: Alarm"]
["00000008","1","03","I2/I1>.Pickup","no","x","Signal: Pickup"]
["00000008","1","04","I2/I1>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000008","1","05","I2/I1>.ExBlo-I","no","x","Module input state: External blocking"]
["00000009","1","00","I2>.Active","no","x","Signal: active"]
["00000009","1","01","I2>.Trip","yes","x","Signal: Trip"]
["00000009","1","02","I2>.Alarm","no","x","Signal: Alarm"]
["00000009","1","03","I2>.Pickup","no","x","Signal: Pickup"]
["00000009","1","04","I2>.IH2 Blo","no","x","Signal: Blocking the trip command by an inrush"]
["00000009","1","05","I2>.ExBlo-I","no","x","Module input state: External blocking"]
["00000010","1","00","ThR.Active","no","x","Signal: active"]
["00000010","1","01","ThR.Trip","yes","x","Signal: Trip"]
["00000010","1","02","ThR.Alarm","no","x","Signal: Alarm"]
["00000010","1","03","ThR.Pickup","no","x","Signal: Pickup"]
["00000010","1","04","ThR.Pre-Alarm","no","x","Signal: The set value for the Θ Threshold has been exceeded."]
["00000010","1","05","ThR.ExBlo-I","no","x","Module input state: External blocking"]
["00000011","1","00","Ipeak>.Active","no","x","Signal: active"]
["00000011","1","01","Ipeak>.Trip","yes","x","Signal: Trip"]
["00000011","1","02","Ipeak>.Alarm","no","x","Signal: Alarm"]
["00000011","1","03","Ipeak>.Pickup","no","x","Signal: Pickup"]
["00000011","1","05","Ipeak>.Trip IA","yes","x","Signal: Trip due to a fault in phase A"]
["00000011","1","06","Ipeak>.Trip IB","yes","x","Signal: Trip due to a fault in phase B"]
["00000011","1","07","Ipeak>.Trip IC","yes","x","Signal: Trip due to a fault in phase C"]
["00000011","1","08","Ipeak>.Alarm IA","no","x","Signal: Alarm due to a fault in phase A"]
["00000011","1","09","Ipeak>.Alarm IB","no","x","Signal: Alarm due to a fault in phase B"]
["00000011","1","10","Ipeak>.Alarm IC","no","x","Signal: Alarm due to a fault in phase C"]
["00000011","1","11","Ipeak>.Pickup IA","no","x","Signal: Pickup in phase A"]
["00000011","1","12","Ipeak>.Pickup IB","no","x","Signal: Pickup in phase B"]
["00000011","1","13","Ipeak>.Pickup IC","no","x","Signal: Pickup in phase C"]
["00000011","1","14","Ipeak>.ExBlo-I","no","x","Module input state: External blocking"]
["00000012","1","00","SOTF.Active","no","x","Signal: active"]
["00000012","1","01","SOTF.Trip","yes","x","Signal: Trip"]
["00000012","1","02","SOTF.Alarm","no","x","Signal: Alarm"]
["00000012","1","03","SOTF.Pickup","no","x","Signal: Pickup"]
["00000012","1","04","SOTF.ExBlo-I","no","x","Module input state: External blocking"]
["00000012","1","05","SOTF.Trigger-I","no","x","State of the module input: Assign the type of pickup signal that triggers the SOTF module. If the assigned pickup signal is issued, the SOTF module itself picks up."]
["00000013","1","00","ExP[1].Active","no","x","Signal: active"]
["00000013","1","01","ExP[1].Trip","yes","x","Signal: Trip"]
["00000013","1","02","ExP[1].Alarm","no","x","Alarm"]
["00000013","1","03","ExP[1].Pickup","no","x","Signal: Pickup"]
["00000013","1","04","ExP[1].ExBlo-I","no","x","Module input state: External blocking"]
["00000013","1","05","ExP[1].Trigger Signal-I","no","x","State of the module input: External trigger signal"]
["00000014","1","00","ExP[2].Active","no","x","Signal: active"]
["00000014","1","01","ExP[2].Trip","yes","x","Signal: Trip"]
["00000014","1","02","ExP[2].Alarm","no","x","Alarm"]
["00000014","1","03","ExP[2].Pickup","no","x","Signal: Pickup"]
["00000014","1","04","ExP[2].ExBlo-I","no","x","Module input state: External blocking"]
["00000014","1","05","ExP[2].Trigger Signal-I","no","x","State of the module input: External trigger signal"]
["00000014","1","06","ExP[2].Condition-I","no","x","State of the module input: Condition for External Protection"]
["00000015","1","00","TCM.Active","no","x","Signal: active"]
["00000015","1","01","TCM.Alarm","no","x","Signal: Alarm"]
["00000015","1","02","TCM.ExBlo-I","no","x","Module input state: External blocking"]
["00000016","1","00","IH2.Active","no","x","Signal: active"]
["00000016","1","01","IH2.Block. A","no","x","Signal: Inrush blocking of phase A of the phase overcurrent protection"]
["00000016","1","02","IH2.Block. B","no","x","Signal: Inrush blocking of phase B of the phase overcurrent protection"]
["00000016","1","03","IH2.Block. C","no","x","Signal: Inrush blocking of phase C of the phase overcurrent protection"]
["00000016","1","04","IH2.Block. Ground","no","x","Signal: Inrush blocking of the ground (earth) overcurrent protection and min. 1 phase of the phase overcurrent protection."]
["00000016","1","05","IH2.Block. 3-ph","no","x","Signal: 3-phase Inrush blocking: An inrush has been detected in (at least) one phase, so that all three phases are blocked."]
["00000016","1","06","IH2.Imax exceeded","no","x","Signal: The Inrush limit value has been exceeded, so that the inrush blocking has been cancelled."]
["00000016","1","07","IH2.tmax elapsed","no","x","Signal: The (phase-selective) maximum duration of an inrush blocking has been reached, so that the inrush blocking has been stopped."]
["00000017","1","00","Life Load.Active","no","x","Signal: active"]
["00000017","1","01","Life Load.Alarm","no","x","Signal: Alarm"]
["00000017","1","02","Life Load.Assign_1_","no","x","Assignement 1 example_"]
["00000018","1","00","CBF.Active","no","x","Signal: active"]
["00000018","1","01","CBF.Alarm","no","x","Signal: Alarm"]
["00000018","1","02","CBF.ExBlo-I","no","x","Module input state: External blocking"]
["00000019","1","00","BkrWear.Active","no","x","Signal: active"]
["00000019","1","01","BkrWear.Alarm","no","x","Signal: Alarm: The maximum number of open commands or the maximum value for the sum of ruptured currents has been exceeded."]
["00000019","1","02","BkrWear.Alm(mx.Sum.Tr)","no","x","Signal: Alarm: The maximum number of open commands has been exceeded."]
["00000019","1","03","BkrWear.Alm(mx.Sum.Itrip)","no","x","Signal: Alarm: The maximum value for the sum of ruptured currents has been exceeded."]
["00000019","1","04","BkrWear.Alm (CB Wear Lev.)","no","x","Signal: Alarm: The maximum wear level of the circuit breaker has been exceeded."]
["00000020","1","00","CLPU.Active","no","x","Signal: active"]
["00000020","1","01","CLPU.detected","no","x","Signal: The CLPU stabilization has been triggered."]
["00000020","1","02","CLPU.stab.","no","x","Signal: The CLPU stabilization is active."]
["00000020","1","03","CLPU.ExBlo-I","no","x","Module input state: External blocking"]

{"sheet":"FC4 (Measurement Data)","index":3,"n_rows":82,"n_cols":10,"rows_kept":82,"cut":false,"hidden":false,"merged":[]}
["Address","Word length","Information Object","Format","Unit","Factor","Scaling","Value Type","filter","Description"]
["00001000","2","CT.IA ","Float","A","1.0","Primary","Actual value","x","Measured value: Phase current (fundamental)"]
["00001002","2","CT.IB ","Float","A","1.0","Primary","Actual value","x","Measured value: Phase current (fundamental)"]
["00001004","2","CT.IC ","Float","A","1.0","Primary","Actual value","x","Measured value: Phase current (fundamental)"]
["00001006","2","CT.IG meas ","Float","A","1.0","Primary","Actual value","x","Measured value (measured): IG (fundamental)"]
["00001008","2","CT.IG calc ","Float","A","1.0","Primary","Actual value","x","Measured value (calculated): IG (fundamental) \nSince the value might be unreliable or invalid for low phase currents it is displayed as “-0.0” in this case."]
["00001010","2","CT.phi IA","Float","°","1.0",".","Actual value","x","Measured value (calculated): Angle of Phasor IA \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00001012","2","CT.phi IB","Float","°","1.0",".","Actual value","x","Measured value (calculated): Angle of Phasor IB \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00001014","2","CT.phi IC","Float","°","1.0",".","Actual value","x","Measured value (calculated): Angle of Phasor IC \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00001016","2","CT.phi IG meas","Float","°","1.0",".","Actual value","x","Measured value (calculated): Angle of Phasor IG meas \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00001020","2","CT.phi IG calc","Float","°","1.0",".","Actual value","x","Measured value (calculated): Angle of Phasor IG calc \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00001022","2","CT.IA H2","Float","%","1.0",".","Actual value","x","Measured Value: Ratio of 2nd harmonic over fundamental of IA"]
["00001024","2","CT.IB H2","Float","%","1.0",".","Actual value","x","Measured Value: Ratio of 2nd harmonic over fundamental of IB"]
["00001026","2","CT.IC H2","Float","%","1.0",".","Actual value","x","Measured Value: Ratio of 2nd harmonic over fundamental of IC"]
["00001028","2","CT.I0 ","Float","A","1.0","Primary","Actual value","x","Measured value (calculated): Zero current (fundamental)"]
["00001030","2","CT.I1 ","Float","A","1.0","Primary","Actual value","x","Measured value (calculated): Positive phase sequence current (fundamental)"]
["00001032","2","CT.I2 ","Float","A","1.0","Primary","Actual value","x","Measured value (calculated): Unbalanced load current (fundamental)"]
["00001034","2","CT.%(I2/I1)","Float","%","1.0",".","Actual value","x","Measured value (calculated): I2/I1, phase sequence will be taken into account automatically."]
["00001036","2","CT.IA RMS","Float","A","1.0","Primary","Actual value","x","Measured value: Phase current (RMS)"]
["00001038","2","CT.IB RMS","Float","A","1.0","Primary","Actual value","x","Measured value: Phase current (RMS)"]
["00001040","2","CT.IC RMS","Float","A","1.0","Primary","Actual value","x","Measured value: Phase current (RMS)"]
["00001042","2","CT.IG meas RMS","Float","A","1.0","Primary","Actual value","x","Measured value (measured): IG (RMS)"]
["00001044","2","CT.IG calc RMS","Float","A","1.0","Primary","Actual value","x","Measured value (calculated): IG (RMS) \nSince the value might be unreliable or invalid for low phase currents it is displayed as “-0.0” in this case."]
["00001046","2","CT.%IA THD","Float","%","1.0",".","Actual value","x","Measured value (calculated): IA Total Harmonic Distortion"]
["00001048","2","CT.%IB THD","Float","%","1.0",".","Actual value","x","Measured value (calculated): IB Total Harmonic Distortion"]
["00001050","2","CT.%IC THD","Float","%","1.0",".","Actual value","x","Measured value (calculated): IC Total Harmonic Distortion"]
["00001052","2","ThR.Therm. Lev.","Float","%","1.0",".","Actual value","x","Measured value: Ongoing thermal level"]
["00001054","2","Peak Current Ptr.Imax","Float","A","1.0","Primary","Actual value","x","Maximum value of the averaged phase current »Iavg« since the last reset"]
["00001056","2","Peak Current Ptr.Iavg","Float","A","1.0","Primary","Actual value","x","Maximum value of the phase current, time-averaged over the set time-window \nAs long as the displayed value of »Iavg« is not significant yet, because the calculation is ongoing, the value is displayed as “-0.0”. (After the set time window has elapsed a valid value is displayed.)"]
["00001058","2","Life Load.< 0.4 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001060","2","Life Load.0.4 ... 0.5 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001062","2","Life Load.0.5 ... 0.6 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001064","2","Life Load.0.6 ... 0.7 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001066","2","Life Load.0.7 ... 0.8 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001068","2","Life Load.0.8 ... 0.9 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001070","2","Life Load.0.9 ... 1.0 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001072","2","Life Load.1.0 ... 1.1 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001074","2","Life Load.1.1 ... 1.2 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001076","2","Life Load.> 1.2 In","Float","d","1.0",".","Actual value","x","Number of operating days with measured current values within this range"]
["00001078","2","Life Load.Time to Alarm","Float","d","1.0",".","Actual value","x","Time (displayed in days) until an alarm signal is issued, because the device has been connected to too high phase currents for a too long time. (The time counts backwards from the »Threshold t« setting to 0. The Direct Command »Rst. Alarm« sets it back to »Threshold t«.)"]
["00001080","2","Sys.Op. Hours","Float","h","1.0",".","Actual value","x","Device operation hours counter, that shows for how long the device has been operating since the last restart."]
["00005000","9","Modbus.Fault rec","Enum (Fault Reasons)",".",".",".",".","x","The communication fault record contains the trip cause and trip time as a structured compound value of words/registers. These are, from low to high address:\n- [word 0, short] RecordNo\n- [Word 1, short] Trip Cause\n- [Word 2, short] Pickup Cause(*)\n- [Word 3, short] Fault No.\n- [Word 4, short] No. of Grid Faults\n- [Word 5 ... Word 8, long long] (WIC returns here only zeros.)\n(*) Code for the trip cause. In case of several simultaneous trip causes the primary cause is selected. If there is another trip later then the new trip cause overwrites the previous one. The codes for the trip cause are documented in the SCADA documentation."]
["00010000","2","Sys.Build","Uint32",".","1.0",".","Actual value","x","Build Number"]
["00010002","8","Sys.DM version","ASCII String. 16 Bytes",".",".",".",".","x","Version of the device model"]
["00010010","8","Sys.SW version","ASCII String. 16 Bytes",".",".",".",".","x","Version of the device firmware"]
["00010018","8","Sys.CAT No.","ASCII String. 16 Bytes",".",".",".",".","x","»CAT No.«, Order Code as printed on the nameplate of the device."]
["00010026","8","Sys.REV.","ASCII String. 16 Bytes",".",".",".",".","x","Revision (as printed on the nameplate of the device)."]
["00010034","8","Sys.S/N","ASCII String. 16 Bytes",".",".",".",".","x","The serial number of the device."]
["00010100","2","Sys.Build","Uint32",".","1.0",".","Actual value","x","Build Number"]
["00010102","8","Sys.DM version","ASCII String. 16 Bytes",".",".",".",".","x","Version of the device model"]
["00010110","8","Sys.SW version","ASCII String. 16 Bytes",".",".",".",".","x","Version of the device firmware"]
["00010118","8","Sys.CAT No.","ASCII String. 16 Bytes",".",".",".",".","x","»CAT No.«, Order Code as printed on the nameplate of the device."]
["00010126","8","Sys.REV.","ASCII String. 16 Bytes",".",".",".",".","x","Revision (as printed on the nameplate of the device)."]
["00010134","8","Sys.S/N","ASCII String. 16 Bytes",".",".",".",".","x","The serial number of the device."]
["00010200","2","TcpIp.Build","Uint32",".","1.0",".","Actual value","x","Build Number"]
["00010202","8","TcpIp.SW version","ASCII String. 16 Bytes",".",".",".",".","x","Version of the device firmware"]
["00010210","8","TcpIp.Interf. Type","ASCII String. 16 Bytes",".",".",".",".","x","Specification of the (built-in) hardware module for the communication interface"]
["00011000","2","CT.IA ","Float","A","1.0","Primary","Fault value","x","Measured value: Phase current (fundamental)"]
["00011002","2","CT.IB ","Float","A","1.0","Primary","Fault value","x","Measured value: Phase current (fundamental)"]
["00011004","2","CT.IC ","Float","A","1.0","Primary","Fault value","x","Measured value: Phase current (fundamental)"]
["00011006","2","CT.IG meas ","Float","A","1.0","Primary","Fault value","x","Measured value (measured): IG (fundamental)"]
["00011008","2","CT.IG calc ","Float","A","1.0","Primary","Fault value","x","Measured value (calculated): IG (fundamental) \nSince the value might be unreliable or invalid for low phase currents it is displayed as “-0.0” in this case."]
["00011010","2","CT.phi IA","Float","°","1.0",".","Fault value","x","Measured value (calculated): Angle of Phasor IA \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00011012","2","CT.phi IB","Float","°","1.0",".","Fault value","x","Measured value (calculated): Angle of Phasor IB \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00011014","2","CT.phi IC","Float","°","1.0",".","Fault value","x","Measured value (calculated): Angle of Phasor IC \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00011016","2","CT.phi IG meas","Float","°","1.0",".","Fault value","x","Measured value (calculated): Angle of Phasor IG meas \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00011020","2","CT.phi IG calc","Float","°","1.0",".","Fault value","x","Measured value (calculated): Angle of Phasor IG calc \nSince the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case."]
["00011022","2","CT.IA H2","Float","%","1.0",".","Fault value","x","Measured Value: Ratio of 2nd harmonic over fundamental of IA"]
["00011024","2","CT.IB H2","Float","%","1.0",".","Fault value","x","Measured Value: Ratio of 2nd harmonic over fundamental of IB"]
["00011026","2","CT.IC H2","Float","%","1.0",".","Fault value","x","Measured Value: Ratio of 2nd harmonic over fundamental of IC"]
["00011028","2","CT.I0 ","Float","A","1.0","Primary","Fault value","x","Measured value (calculated): Zero current (fundamental)"]
["00011030","2","CT.I1 ","Float","A","1.0","Primary","Fault value","x","Measured value (calculated): Positive phase sequence current (fundamental)"]
["00011032","2","CT.I2 ","Float","A","1.0","Primary","Fault value","x","Measured value (calculated): Unbalanced load current (fundamental)"]
["00011034","2","CT.%(I2/I1)","Float","%","1.0",".","Fault value","x","Measured value (calculated): I2/I1, phase sequence will be taken into account automatically."]
["00011036","2","CT.IA RMS","Float","A","1.0","Primary","Fault value","x","Measured value: Phase current (RMS)"]
["00011038","2","CT.IB RMS","Float","A","1.0","Primary","Fault value","x","Measured value: Phase current (RMS)"]
["00011040","2","CT.IC RMS","Float","A","1.0","Primary","Fault value","x","Measured value: Phase current (RMS)"]
["00011042","2","CT.IG meas RMS","Float","A","1.0","Primary","Fault value","x","Measured value (measured): IG (RMS)"]
["00011044","2","CT.IG calc RMS","Float","A","1.0","Primary","Fault value","x","Measured value (calculated): IG (RMS) \nSince the value might be unreliable or invalid for low phase currents it is displayed as “-0.0” in this case."]
["00011052","2","ThR.Therm. Lev.","Float","%","1.0",".","Fault value","x","Measured value: Ongoing thermal level"]
[]
["Note for primary: For reading primary value, the current transformer should be defined in the device via [File Para / CT] CT.CT pri. Otherwise responses on these value requests will be zero."]

{"sheet":"FC5 (Single Commands)","index":4,"n_rows":10,"n_cols":3,"rows_kept":10,"cut":false,"hidden":false,"merged":[]}
["Address","Information Object","Description"]
["00002000","Modbus.Scada","Direct Command to reset all Modbus-latched states.(Latched in Map)."]
["00002001","Modbus.Rst. Counters","Direct Command to reset all Modbus Diagnosis Counters"]
["00002002","Prot.Rst. LEDs, FIs","Direct Command to immediately reset all latched LEDs, all DiggiMEC Flag Indicators, and the Fault Info Screen that might be visible on the DiggiMEC display."]
["00002003","Prot.Rst. Alm/Flt Rec.","Direct Command to immediately delete all entries from the Alarm/Fault Recorder."]
["00002004","ThR.Rst. Thermal Lev.","Reset the thermal level"]
["00002005","Sys.Rst. Err. LED","Direct Command to acknowledge a (device-internal) error. This also resets the System (Ready/Error) LED."]
["00002006","BkrWear.Reset","Direct Command to reset the counters and the wear level of the circuit breaker."]
["00002007","Peak Current Ptr.Clear","Direct Command to reset the drag indicator for »Imax«"]
["00002008","Life Load.Rst. Alarm","Direct Command to reset the Alarm signal. This also resets the countdown timer »Time to Alarm« back to the setting value »Threshold t«."]

{"sheet":"Enum (Fault Reasons)","index":5,"n_rows":30,"n_cols":3,"rows_kept":30,"cut":false,"hidden":false,"merged":[]}
["Value","Module","Description"]
["1","Prot","Module General Protection"]
["2","CT","Current Transformer"]
["5","DiggiMEC","DiggiMEC"]
["6","Sys","System"]
["7","Sgen","Sine wave generator"]
["8","TcpIp","TcpIp"]
["10","IH2","Module Inrush"]
["11","I>","Phase Overcurrent Stage"]
["12","I>>","Phase Overcurrent Stage"]
["13","I>>>","Phase Overcurrent Stage"]
["14","IG>","Ground (earth) current protection stage"]
["15","IG>>","Ground (earth) current protection stage"]
["16","Ipeak>","Peak-Value Overcurrent"]
["17","I2/I1>","Unbalanced Load Protection"]
["18","I2>","Negative-Sequence Current Protection"]
["19","ThR","Thermal replica module"]
["20","SOTF","Switch Onto Fault - Module"]
["21","CLPU","Cold Load Pickup Module"]
["22","ExP[1]","External Protection - Module"]
["23","ExP[2]","External Protection - Module"]
["30","TCM","Trip Circuit Monitoring"]
["31","CBF","Circuit breaker failure protection module"]
["32","BkrWear","Breaker Wear"]
["33","SBM","Station Battery Monitoring"]
["58","Life Load","Load Current Histogram"]
["59","Peak Current Ptr","Statistic of the current measuring values"]
["60","Modbus","Modbus"]
[]
["Note: Not all modules cause fault recorder records to be stored."]