## Version
Name | Info
Device | WIC1
DM version | 2.3.007
Build | 65353

## FC1 (State Information)
Address | Information Object | Latched | filter | Description
00000001 | Prot.Active | no | x | Signal: active
00000002 | Prot.Alarm | no | x | Signal: General Alarm
00000003 | Prot.Pickup | no | x | Signal: General Pickup
00000004 | Prot.Trip | yes | x | Signal: General Trip
00000005 | Prot.TripCmd | yes | x | Signal: Trip Command
00000006 | Prot.Pickup IA | no | x | Signal: General Pickup due to a fault in phase A
00000007 | Prot.Pickup IB | no | x | Signal: General Pickup due to a fault in phase B
00000008 | Prot.Pickup IC | no | x | Signal: General Pickup due to a fault in phase C
00000009 | Prot.Pickup IG | no | x | Signal: General Pickup due to a ground current fault
00000010 | Prot.Pickup I Ph | no | x | Signal: General Pickup due to a phase current fault
00000011 | Prot.Pickup Ext. | no | x | Signal: General Pickup due to an external signal
00000012 | Prot.Trip IA | yes | x | Signal: General Trip due to a fault in phase A
00000013 | Prot.Trip IB | yes | x | Signal: General Trip due to a fault in phase B
00000014 | Prot.Trip IC | yes | x | Signal: General Trip due to a fault in phase C
00000015 | Prot.Trip IG | yes | x | Signal: General Trip due to a ground current fault
00000016 | Prot.Trip IPh | yes | x | Signal: General Trip due to a phase current fault
00000017 | Prot.Trip Ext. | yes | x | Signal: General Trip due to an external signal
00000018 | Prot.Pos ON | no | x | Signal: Circuit Breaker is in ON-Position
00000019 | Prot.Pos OFF | no | x | Signal: Circuit Breaker is in OFF-Position
00000020 | Prot.Syst. OK. & Ext.Suppl. | no | x | Signal: The WIC1 is running and is supplied by external auxiliary power and has loaded sufficient electrical energy for triggering the trip impulse output.
00000021 | Prot.DI 1 | no | x | Signal: Digital Input
00000022 | Prot.DI 2 | no | x | Signal: Digital Input
00000023 | Prot.ExBlo TripCmd-I | no | x | Module input state: External Blocking of the Trip Command
00000024 | Prot.ON Cmd | no | x | Signal: ON command issued to the breaker
00000025 | I>.Active | no | x | Signal: active
00000026 | I>.Trip | yes | x | Signal: Trip
00000027 | I>.Alarm | no | x | Signal: Alarm
00000028 | I>.Pickup | no | x | Signal: Pickup
00000029 | I>.Trip IA | yes | x | Signal: Trip due to a fault in phase A
00000030 | I>.Trip IB | yes | x | Signal: Trip due to a fault in phase B
00000031 | I>.Trip IC | yes | x | Signal: Trip due to a fault in phase C
00000032 | I>.Alarm IA | no | x | Signal: Alarm due to a fault in phase A
00000033 | I>.Alarm IB | no | x | Signal: Alarm due to a fault in phase B
00000034 | I>.Alarm IC | no | x | Signal: Alarm due to a fault in phase C
00000035 | I>.Pickup IA | no | x | Signal: Pickup in phase A
00000036 | I>.Pickup IB | no | x | Signal: Pickup in phase B
00000037 | I>.Pickup IC | no | x | Signal: Pickup in phase C
00000038 | I>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000039 | I>.ExBlo-I | no | x | Module input state: External blocking
00000040 | I>>.Active | no | x | Signal: active
00000041 | I>>.Trip | yes | x | Signal: Trip
00000042 | I>>.Alarm | no | x | Signal: Alarm
00000043 | I>>.Pickup | no | x | Signal: Pickup
00000044 | I>>.Trip IA | yes | x | Signal: Trip due to a fault in phase A
00000045 | I>>.Trip IB | yes | x | Signal: Trip due to a fault in phase B
00000046 | I>>.Trip IC | yes | x | Signal: Trip due to a fault in phase C
00000047 | I>>.Alarm IA | no | x | Signal: Alarm due to a fault in phase A
00000048 | I>>.Alarm IB | no | x | Signal: Alarm due to a fault in phase B
00000049 | I>>.Alarm IC | no | x | Signal: Alarm due to a fault in phase C
00000050 | I>>.Pickup IA | no | x | Signal: Pickup in phase A
00000051 | I>>.Pickup IB | no | x | Signal: Pickup in phase B
00000052 | I>>.Pickup IC | no | x | Signal: Pickup in phase C
00000053 | I>>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000054 | I>>.ExBlo-I | no | x | Module input state: External blocking
00000055 | I>>>.Active | no | x | Signal: active
00000056 | I>>>.Trip | yes | x | Signal: Trip
00000057 | I>>>.Alarm | no | x | Signal: Alarm
00000058 | I>>>.Pickup | no | x | Signal: Pickup
00000059 | I>>>.Trip IA | yes | x | Signal: Trip due to a fault in phase A
00000060 | I>>>.Trip IB | yes | x | Signal: Trip due to a fault in phase B
00000061 | I>>>.Trip IC | yes | x | Signal: Trip due to a fault in phase C
00000062 | I>>>.Alarm IA | no | x | Signal: Alarm due to a fault in phase A
00000063 | I>>>.Alarm IB | no | x | Signal: Alarm due to a fault in phase B
00000064 | I>>>.Alarm IC | no | x | Signal: Alarm due to a fault in phase C
00000065 | I>>>.Pickup IA | no | x | Signal: Pickup in phase A
00000066 | I>>>.Pickup IB | no | x | Signal: Pickup in phase B
00000067 | I>>>.Pickup IC | no | x | Signal: Pickup in phase C
00000068 | I>>>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000069 | I>>>.ExBlo-I | no | x | Module input state: External blocking
00000070 | IG>.Active | no | x | Signal: active
00000071 | IG>.Trip | yes | x | Signal: Trip
00000072 | IG>.Alarm | no | x | Signal: Alarm
00000073 | IG>.Pickup | no | x | Signal: Pickup
00000074 | IG>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000075 | IG>.ExBlo-I | no | x | Module input state: External blocking
00000076 | IG>>.Active | no | x | Signal: active
00000077 | IG>>.Trip | yes | x | Signal: Trip
00000078 | IG>>.Alarm | no | x | Signal: Alarm
00000079 | IG>>.Pickup | no | x | Signal: Pickup
00000080 | IG>>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000081 | IG>>.ExBlo-I | no | x | Module input state: External blocking
00000082 | I2/I1>.Active | no | x | Signal: active
00000083 | I2/I1>.Trip | yes | x | Signal: Trip
00000084 | I2/I1>.Alarm | no | x | Signal: Alarm
00000085 | I2/I1>.Pickup | no | x | Signal: Pickup
00000086 | I2/I1>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000087 | I2/I1>.ExBlo-I | no | x | Module input state: External blocking
00000088 | I2>.Active | no | x | Signal: active
00000089 | I2>.Trip | yes | x | Signal: Trip
00000090 | I2>.Alarm | no | x | Signal: Alarm
00000091 | I2>.Pickup | no | x | Signal: Pickup
00000092 | I2>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000093 | I2>.ExBlo-I | no | x | Module input state: External blocking
00000094 | ThR.Active | no | x | Signal: active
00000095 | ThR.Trip | yes | x | Signal: Trip
00000096 | ThR.Alarm | no | x | Signal: Alarm
00000097 | ThR.Pickup | no | x | Signal: Pickup
00000098 | ThR.Pre-Alarm | no | x | Signal: The set value for the Θ Threshold has been exceeded.
00000099 | ThR.ExBlo-I | no | x | Module input state: External blocking
00000100 | Ipeak>.Active | no | x | Signal: active
00000101 | Ipeak>.Trip | yes | x | Signal: Trip
00000102 | Ipeak>.Alarm | no | x | Signal: Alarm
00000103 | Ipeak>.Pickup | no | x | Signal: Pickup
00000104 | Ipeak>.Trip IA | yes | x | Signal: Trip due to a fault in phase A
00000105 | Ipeak>.Trip IB | yes | x | Signal: Trip due to a fault in phase B
00000106 | Ipeak>.Trip IC | yes | x | Signal: Trip due to a fault in phase C
00000107 | Ipeak>.Alarm IA | no | x | Signal: Alarm due to a fault in phase A
00000108 | Ipeak>.Alarm IB | no | x | Signal: Alarm due to a fault in phase B
00000109 | Ipeak>.Alarm IC | no | x | Signal: Alarm due to a fault in phase C
00000110 | Ipeak>.Pickup IA | no | x | Signal: Pickup in phase A
00000111 | Ipeak>.Pickup IB | no | x | Signal: Pickup in phase B
00000112 | Ipeak>.Pickup IC | no | x | Signal: Pickup in phase C
00000113 | Ipeak>.ExBlo-I | no | x | Module input state: External blocking
00000114 | SOTF.Active | no | x | Signal: active
00000115 | SOTF.Trip | yes | x | Signal: Trip
00000116 | SOTF.Alarm | no | x | Signal: Alarm
00000117 | SOTF.Pickup | no | x | Signal: Pickup
00000118 | SOTF.ExBlo-I | no | x | Module input state: External blocking
00000119 | SOTF.Trigger-I | no | x | State of the module input: Assign the type of pickup signal that triggers the SOTF module. If the assigned pickup signal is issued, the SOTF module itself picks up.
00000120 | ExP[1].Active | no | x | Signal: active
00000121 | ExP[1].Trip | yes | x | Signal: Trip
00000122 | ExP[1].Alarm | no | x | Alarm
00000123 | ExP[1].Pickup | no | x | Signal: Pickup
00000124 | ExP[1].ExBlo-I | no | x | Module input state: External blocking
00000125 | ExP[1].Trigger Signal-I | no | x | State of the module input: External trigger signal
00000126 | ExP[2].Active | no | x | Signal: active
00000127 | ExP[2].Trip | yes | x | Signal: Trip
00000128 | ExP[2].Alarm | no | x | Alarm
00000129 | ExP[2].Pickup | no | x | Signal: Pickup
00000130 | ExP[2].ExBlo-I | no | x | Module input state: External blocking
00000131 | ExP[2].Trigger Signal-I | no | x | State of the module input: External trigger signal
00000132 | ExP[2].Condition-I | no | x | State of the module input: Condition for External Protection
00000133 | TCM.Active | no | x | Signal: active
00000134 | TCM.Alarm | no | x | Signal: Alarm
00000135 | TCM.ExBlo-I | no | x | Module input state: External blocking
00000136 | IH2.Active | no | x | Signal: active
00000137 | IH2.Block. A | no | x | Signal: Inrush blocking of phase A of the phase overcurrent protection
00000138 | IH2.Block. B | no | x | Signal: Inrush blocking of phase B of the phase overcurrent protection
00000139 | IH2.Block. C | no | x | Signal: Inrush blocking of phase C of the phase overcurrent protection
00000140 | IH2.Block. Ground | no | x | Signal: Inrush blocking of the ground (earth) overcurrent protection and min. 1 phase of the phase overcurrent protection.
00000141 | IH2.Block. 3-ph | no | x | Signal: 3-phase Inrush blocking: An inrush has been detected in (at least) one phase, so that all three phases are blocked.
00000142 | IH2.Imax exceeded | no | x | Signal: The Inrush limit value has been exceeded, so that the inrush blocking has been cancelled.
00000143 | IH2.tmax elapsed | no | x | Signal: The (phase-selective) maximum duration of an inrush blocking has been reached, so that the inrush blocking has been stopped.
00000144 | Life Load.Active | no | x | Signal: active
00000145 | Life Load.Alarm | no | x | Signal: Alarm
00000146 | Life Load.Assign_1_ | no | x | Assignement 1 example_
00000147 | CBF.Active | no | x | Signal: active
00000148 | CBF.Alarm | no | x | Signal: Alarm
00000149 | CBF.ExBlo-I | no | x | Module input state: External blocking
00000150 | BkrWear.Active | no | x | Signal: active
00000151 | BkrWear.Alarm | no | x | Signal: Alarm: The maximum number of open commands or the maximum value for the sum of ruptured currents has been exceeded.
00000152 | BkrWear.Alm(mx.Sum.Tr) | no | x | Signal: Alarm: The maximum number of open commands has been exceeded.
00000153 | BkrWear.Alm(mx.Sum.Itrip) | no | x | Signal: Alarm: The maximum value for the sum of ruptured currents has been exceeded.
00000154 | BkrWear.Alm (CB Wear Lev.) | no | x | Signal: Alarm: The maximum wear level of the circuit breaker has been exceeded.
00000155 | CLPU.Active | no | x | Signal: active
00000156 | CLPU.detected | no | x | Signal: The CLPU stabilization has been triggered.
00000157 | CLPU.stab. | no | x | Signal: The CLPU stabilization is active.
00000158 | CLPU.ExBlo-I | no | x | Module input state: External blocking

## FC3 (State Information)
Address | Bit size | Bit position | Information Object | Latched | filter | Description
00000001 | 1 | 00 | Prot.Active | no | x | Signal: active
00000001 | 1 | 01 | Prot.Alarm | no | x | Signal: General Alarm
00000001 | 1 | 02 | Prot.Pickup | no | x | Signal: General Pickup
00000001 | 1 | 03 | Prot.Trip | yes | x | Signal: General Trip
00000001 | 1 | 04 | Prot.TripCmd | yes | x | Signal: Trip Command
00000001 | 1 | 05 | Prot.Pickup IA | no | x | Signal: General Pickup due to a fault in phase A
00000001 | 1 | 06 | Prot.Pickup IB | no | x | Signal: General Pickup due to a fault in phase B
00000001 | 1 | 07 | Prot.Pickup IC | no | x | Signal: General Pickup due to a fault in phase C
00000001 | 1 | 08 | Prot.Pickup IG | no | x | Signal: General Pickup due to a ground current fault
00000001 | 1 | 09 | Prot.Pickup I Ph | no | x | Signal: General Pickup due to a phase current fault
00000001 | 1 | 10 | Prot.Pickup Ext. | no | x | Signal: General Pickup due to an external signal
00000001 | 1 | 11 | Prot.Trip IA | yes | x | Signal: General Trip due to a fault in phase A
00000001 | 1 | 12 | Prot.Trip IB | yes | x | Signal: General Trip due to a fault in phase B
00000001 | 1 | 13 | Prot.Trip IC | yes | x | Signal: General Trip due to a fault in phase C
00000001 | 1 | 14 | Prot.Trip IG | yes | x | Signal: General Trip due to a ground current fault
00000001 | 1 | 15 | Prot.Trip IPh | yes | x | Signal: General Trip due to a phase current fault
00000002 | 1 | 00 | Prot.Trip Ext. | yes | x | Signal: General Trip due to an external signal
00000002 | 1 | 01 | Prot.Pos ON | no | x | Signal: Circuit Breaker is in ON-Position
00000002 | 1 | 02 | Prot.Pos OFF | no | x | Signal: Circuit Breaker is in OFF-Position
00000002 | 1 | 03 | Prot.Syst. OK. & Ext.Suppl. | no | x | Signal: The WIC1 is running and is supplied by external auxiliary power and has loaded sufficient electrical energy for triggering the trip impulse output.
00000002 | 1 | 04 | Prot.DI 1 | no | x | Signal: Digital Input
00000002 | 1 | 05 | Prot.DI 2 | no | x | Signal: Digital Input
00000002 | 1 | 06 | Prot.ExBlo TripCmd-I | no | x | Module input state: External Blocking of the Trip Command
00000002 | 1 | 07 | Prot.ON Cmd | no | x | Signal: ON command issued to the breaker
00000003 | 1 | 00 | I>.Active | no | x | Signal: active
00000003 | 1 | 01 | I>.Trip | yes | x | Signal: Trip
00000003 | 1 | 02 | I>.Alarm | no | x | Signal: Alarm
00000003 | 1 | 03 | I>.Pickup | no | x | Signal: Pickup
00000003 | 1 | 04 | I>.Trip IA | yes | x | Signal: Trip due to a fault in phase A
00000003 | 1 | 05 | I>.Trip IB | yes | x | Signal: Trip due to a fault in phase B
00000003 | 1 | 06 | I>.Trip IC | yes | x | Signal: Trip due to a fault in phase C
00000003 | 1 | 07 | I>.Alarm IA | no | x | Signal: Alarm due to a fault in phase A
00000003 | 1 | 08 | I>.Alarm IB | no | x | Signal: Alarm due to a fault in phase B
00000003 | 1 | 09 | I>.Alarm IC | no | x | Signal: Alarm due to a fault in phase C
00000003 | 1 | 10 | I>.Pickup IA | no | x | Signal: Pickup in phase A
00000003 | 1 | 11 | I>.Pickup IB | no | x | Signal: Pickup in phase B
00000003 | 1 | 12 | I>.Pickup IC | no | x | Signal: Pickup in phase C
00000003 | 1 | 13 | I>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000003 | 1 | 14 | I>.ExBlo-I | no | x | Module input state: External blocking
00000004 | 1 | 00 | I>>.Active | no | x | Signal: active
00000004 | 1 | 01 | I>>.Trip | yes | x | Signal: Trip
00000004 | 1 | 02 | I>>.Alarm | no | x | Signal: Alarm
00000004 | 1 | 03 | I>>.Pickup | no | x | Signal: Pickup
00000004 | 1 | 04 | I>>.Trip IA | yes | x | Signal: Trip due to a fault in phase A
00000004 | 1 | 05 | I>>.Trip IB | yes | x | Signal: Trip due to a fault in phase B
00000004 | 1 | 06 | I>>.Trip IC | yes | x | Signal: Trip due to a fault in phase C
00000004 | 1 | 07 | I>>.Alarm IA | no | x | Signal: Alarm due to a fault in phase A
00000004 | 1 | 08 | I>>.Alarm IB | no | x | Signal: Alarm due to a fault in phase B
00000004 | 1 | 09 | I>>.Alarm IC | no | x | Signal: Alarm due to a fault in phase C
00000004 | 1 | 10 | I>>.Pickup IA | no | x | Signal: Pickup in phase A
00000004 | 1 | 11 | I>>.Pickup IB | no | x | Signal: Pickup in phase B
00000004 | 1 | 12 | I>>.Pickup IC | no | x | Signal: Pickup in phase C
00000004 | 1 | 13 | I>>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000004 | 1 | 14 | I>>.ExBlo-I | no | x | Module input state: External blocking
00000005 | 1 | 00 | I>>>.Active | no | x | Signal: active
00000005 | 1 | 01 | I>>>.Trip | yes | x | Signal: Trip
00000005 | 1 | 02 | I>>>.Alarm | no | x | Signal: Alarm
00000005 | 1 | 03 | I>>>.Pickup | no | x | Signal: Pickup
00000005 | 1 | 04 | I>>>.Trip IA | yes | x | Signal: Trip due to a fault in phase A
00000005 | 1 | 05 | I>>>.Trip IB | yes | x | Signal: Trip due to a fault in phase B
00000005 | 1 | 06 | I>>>.Trip IC | yes | x | Signal: Trip due to a fault in phase C
00000005 | 1 | 07 | I>>>.Alarm IA | no | x | Signal: Alarm due to a fault in phase A
00000005 | 1 | 08 | I>>>.Alarm IB | no | x | Signal: Alarm due to a fault in phase B
00000005 | 1 | 09 | I>>>.Alarm IC | no | x | Signal: Alarm due to a fault in phase C
00000005 | 1 | 10 | I>>>.Pickup IA | no | x | Signal: Pickup in phase A
00000005 | 1 | 11 | I>>>.Pickup IB | no | x | Signal: Pickup in phase B
00000005 | 1 | 12 | I>>>.Pickup IC | no | x | Signal: Pickup in phase C
00000005 | 1 | 13 | I>>>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000005 | 1 | 14 | I>>>.ExBlo-I | no | x | Module input state: External blocking
00000006 | 1 | 00 | IG>.Active | no | x | Signal: active
00000006 | 1 | 01 | IG>.Trip | yes | x | Signal: Trip
00000006 | 1 | 02 | IG>.Alarm | no | x | Signal: Alarm
00000006 | 1 | 03 | IG>.Pickup | no | x | Signal: Pickup
00000006 | 1 | 04 | IG>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000006 | 1 | 05 | IG>.ExBlo-I | no | x | Module input state: External blocking
00000007 | 1 | 00 | IG>>.Active | no | x | Signal: active
00000007 | 1 | 01 | IG>>.Trip | yes | x | Signal: Trip
00000007 | 1 | 02 | IG>>.Alarm | no | x | Signal: Alarm
00000007 | 1 | 03 | IG>>.Pickup | no | x | Signal: Pickup
00000007 | 1 | 04 | IG>>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000007 | 1 | 05 | IG>>.ExBlo-I | no | x | Module input state: External blocking
00000008 | 1 | 00 | I2/I1>.Active | no | x | Signal: active
00000008 | 1 | 01 | I2/I1>.Trip | yes | x | Signal: Trip
00000008 | 1 | 02 | I2/I1>.Alarm | no | x | Signal: Alarm
00000008 | 1 | 03 | I2/I1>.Pickup | no | x | Signal: Pickup
00000008 | 1 | 04 | I2/I1>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000008 | 1 | 05 | I2/I1>.ExBlo-I | no | x | Module input state: External blocking
00000009 | 1 | 00 | I2>.Active | no | x | Signal: active
00000009 | 1 | 01 | I2>.Trip | yes | x | Signal: Trip
00000009 | 1 | 02 | I2>.Alarm | no | x | Signal: Alarm
00000009 | 1 | 03 | I2>.Pickup | no | x | Signal: Pickup
00000009 | 1 | 04 | I2>.IH2 Blo | no | x | Signal: Blocking the trip command by an inrush
00000009 | 1 | 05 | I2>.ExBlo-I | no | x | Module input state: External blocking
00000010 | 1 | 00 | ThR.Active | no | x | Signal: active
00000010 | 1 | 01 | ThR.Trip | yes | x | Signal: Trip
00000010 | 1 | 02 | ThR.Alarm | no | x | Signal: Alarm
00000010 | 1 | 03 | ThR.Pickup | no | x | Signal: Pickup
00000010 | 1 | 04 | ThR.Pre-Alarm | no | x | Signal: The set value for the Θ Threshold has been exceeded.
00000010 | 1 | 05 | ThR.ExBlo-I | no | x | Module input state: External blocking
00000011 | 1 | 00 | Ipeak>.Active | no | x | Signal: active
00000011 | 1 | 01 | Ipeak>.Trip | yes | x | Signal: Trip
00000011 | 1 | 02 | Ipeak>.Alarm | no | x | Signal: Alarm
00000011 | 1 | 03 | Ipeak>.Pickup | no | x | Signal: Pickup
00000011 | 1 | 05 | Ipeak>.Trip IA | yes | x | Signal: Trip due to a fault in phase A
00000011 | 1 | 06 | Ipeak>.Trip IB | yes | x | Signal: Trip due to a fault in phase B
00000011 | 1 | 07 | Ipeak>.Trip IC | yes | x | Signal: Trip due to a fault in phase C
00000011 | 1 | 08 | Ipeak>.Alarm IA | no | x | Signal: Alarm due to a fault in phase A
00000011 | 1 | 09 | Ipeak>.Alarm IB | no | x | Signal: Alarm due to a fault in phase B
00000011 | 1 | 10 | Ipeak>.Alarm IC | no | x | Signal: Alarm due to a fault in phase C
00000011 | 1 | 11 | Ipeak>.Pickup IA | no | x | Signal: Pickup in phase A
00000011 | 1 | 12 | Ipeak>.Pickup IB | no | x | Signal: Pickup in phase B
00000011 | 1 | 13 | Ipeak>.Pickup IC | no | x | Signal: Pickup in phase C
00000011 | 1 | 14 | Ipeak>.ExBlo-I | no | x | Module input state: External blocking
00000012 | 1 | 00 | SOTF.Active | no | x | Signal: active
00000012 | 1 | 01 | SOTF.Trip | yes | x | Signal: Trip
00000012 | 1 | 02 | SOTF.Alarm | no | x | Signal: Alarm
00000012 | 1 | 03 | SOTF.Pickup | no | x | Signal: Pickup
00000012 | 1 | 04 | SOTF.ExBlo-I | no | x | Module input state: External blocking
00000012 | 1 | 05 | SOTF.Trigger-I | no | x | State of the module input: Assign the type of pickup signal that triggers the SOTF module. If the assigned pickup signal is issued, the SOTF module itself picks up.
00000013 | 1 | 00 | ExP[1].Active | no | x | Signal: active
00000013 | 1 | 01 | ExP[1].Trip | yes | x | Signal: Trip
00000013 | 1 | 02 | ExP[1].Alarm | no | x | Alarm
00000013 | 1 | 03 | ExP[1].Pickup | no | x | Signal: Pickup
00000013 | 1 | 04 | ExP[1].ExBlo-I | no | x | Module input state: External blocking
00000013 | 1 | 05 | ExP[1].Trigger Signal-I | no | x | State of the module input: External trigger signal
00000014 | 1 | 00 | ExP[2].Active | no | x | Signal: active
00000014 | 1 | 01 | ExP[2].Trip | yes | x | Signal: Trip
00000014 | 1 | 02 | ExP[2].Alarm | no | x | Alarm
00000014 | 1 | 03 | ExP[2].Pickup | no | x | Signal: Pickup
00000014 | 1 | 04 | ExP[2].ExBlo-I | no | x | Module input state: External blocking
00000014 | 1 | 05 | ExP[2].Trigger Signal-I | no | x | State of the module input: External trigger signal
00000014 | 1 | 06 | ExP[2].Condition-I | no | x | State of the module input: Condition for External Protection
00000015 | 1 | 00 | TCM.Active | no | x | Signal: active
00000015 | 1 | 01 | TCM.Alarm | no | x | Signal: Alarm
00000015 | 1 | 02 | TCM.ExBlo-I | no | x | Module input state: External blocking
00000016 | 1 | 00 | IH2.Active | no | x | Signal: active
00000016 | 1 | 01 | IH2.Block. A | no | x | Signal: Inrush blocking of phase A of the phase overcurrent protection
00000016 | 1 | 02 | IH2.Block. B | no | x | Signal: Inrush blocking of phase B of the phase overcurrent protection
00000016 | 1 | 03 | IH2.Block. C | no | x | Signal: Inrush blocking of phase C of the phase overcurrent protection
00000016 | 1 | 04 | IH2.Block. Ground | no | x | Signal: Inrush blocking of the ground (earth) overcurrent protection and min. 1 phase of the phase overcurrent protection.
00000016 | 1 | 05 | IH2.Block. 3-ph | no | x | Signal: 3-phase Inrush blocking: An inrush has been detected in (at least) one phase, so that all three phases are blocked.
00000016 | 1 | 06 | IH2.Imax exceeded | no | x | Signal: The Inrush limit value has been exceeded, so that the inrush blocking has been cancelled.
00000016 | 1 | 07 | IH2.tmax elapsed | no | x | Signal: The (phase-selective) maximum duration of an inrush blocking has been reached, so that the inrush blocking has been stopped.
00000017 | 1 | 00 | Life Load.Active | no | x | Signal: active
00000017 | 1 | 01 | Life Load.Alarm | no | x | Signal: Alarm
00000017 | 1 | 02 | Life Load.Assign_1_ | no | x | Assignement 1 example_
00000018 | 1 | 00 | CBF.Active | no | x | Signal: active
00000018 | 1 | 01 | CBF.Alarm | no | x | Signal: Alarm
00000018 | 1 | 02 | CBF.ExBlo-I | no | x | Module input state: External blocking
00000019 | 1 | 00 | BkrWear.Active | no | x | Signal: active
00000019 | 1 | 01 | BkrWear.Alarm | no | x | Signal: Alarm: The maximum number of open commands or the maximum value for the sum of ruptured currents has been exceeded.
00000019 | 1 | 02 | BkrWear.Alm(mx.Sum.Tr) | no | x | Signal: Alarm: The maximum number of open commands has been exceeded.
00000019 | 1 | 03 | BkrWear.Alm(mx.Sum.Itrip) | no | x | Signal: Alarm: The maximum value for the sum of ruptured currents has been exceeded.
00000019 | 1 | 04 | BkrWear.Alm (CB Wear Lev.) | no | x | Signal: Alarm: The maximum wear level of the circuit breaker has been exceeded.
00000020 | 1 | 00 | CLPU.Active | no | x | Signal: active
00000020 | 1 | 01 | CLPU.detected | no | x | Signal: The CLPU stabilization has been triggered.
00000020 | 1 | 02 | CLPU.stab. | no | x | Signal: The CLPU stabilization is active.
00000020 | 1 | 03 | CLPU.ExBlo-I | no | x | Module input state: External blocking

## FC4 (Measurement Data)
Address | Word length | Information Object | Format | Unit | Factor | Scaling | Value Type | filter | Description
00001000 | 2 | CT.IA | Float | A | 1.0 | Primary | Actual value | x | Measured value: Phase current (fundamental)
00001002 | 2 | CT.IB | Float | A | 1.0 | Primary | Actual value | x | Measured value: Phase current (fundamental)
00001004 | 2 | CT.IC | Float | A | 1.0 | Primary | Actual value | x | Measured value: Phase current (fundamental)
00001006 | 2 | CT.IG meas | Float | A | 1.0 | Primary | Actual value | x | Measured value (measured): IG (fundamental)
00001008 | 2 | CT.IG calc | Float | A | 1.0 | Primary | Actual value | x | Measured value (calculated): IG (fundamental) Since the value might be unreliable or invalid for low phase currents it is displayed as “-0.0” in this case.
00001010 | 2 | CT.phi IA | Float | ° | 1.0 | . | Actual value | x | Measured value (calculated): Angle of Phasor IA Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00001012 | 2 | CT.phi IB | Float | ° | 1.0 | . | Actual value | x | Measured value (calculated): Angle of Phasor IB Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00001014 | 2 | CT.phi IC | Float | ° | 1.0 | . | Actual value | x | Measured value (calculated): Angle of Phasor IC Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00001016 | 2 | CT.phi IG meas | Float | ° | 1.0 | . | Actual value | x | Measured value (calculated): Angle of Phasor IG meas Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00001020 | 2 | CT.phi IG calc | Float | ° | 1.0 | . | Actual value | x | Measured value (calculated): Angle of Phasor IG calc Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00001022 | 2 | CT.IA H2 | Float | % | 1.0 | . | Actual value | x | Measured Value: Ratio of 2nd harmonic over fundamental of IA
00001024 | 2 | CT.IB H2 | Float | % | 1.0 | . | Actual value | x | Measured Value: Ratio of 2nd harmonic over fundamental of IB
00001026 | 2 | CT.IC H2 | Float | % | 1.0 | . | Actual value | x | Measured Value: Ratio of 2nd harmonic over fundamental of IC
00001028 | 2 | CT.I0 | Float | A | 1.0 | Primary | Actual value | x | Measured value (calculated): Zero current (fundamental)
00001030 | 2 | CT.I1 | Float | A | 1.0 | Primary | Actual value | x | Measured value (calculated): Positive phase sequence current (fundamental)
00001032 | 2 | CT.I2 | Float | A | 1.0 | Primary | Actual value | x | Measured value (calculated): Unbalanced load current (fundamental)
00001034 | 2 | CT.%(I2/I1) | Float | % | 1.0 | . | Actual value | x | Measured value (calculated): I2/I1, phase sequence will be taken into account automatically.
00001036 | 2 | CT.IA RMS | Float | A | 1.0 | Primary | Actual value | x | Measured value: Phase current (RMS)
00001038 | 2 | CT.IB RMS | Float | A | 1.0 | Primary | Actual value | x | Measured value: Phase current (RMS)
00001040 | 2 | CT.IC RMS | Float | A | 1.0 | Primary | Actual value | x | Measured value: Phase current (RMS)
00001042 | 2 | CT.IG meas RMS | Float | A | 1.0 | Primary | Actual value | x | Measured value (measured): IG (RMS)
00001044 | 2 | CT.IG calc RMS | Float | A | 1.0 | Primary | Actual value | x | Measured value (calculated): IG (RMS) Since the value might be unreliable or invalid for low phase currents it is displayed as “-0.0” in this case.
00001046 | 2 | CT.%IA THD | Float | % | 1.0 | . | Actual value | x | Measured value (calculated): IA Total Harmonic Distortion
00001048 | 2 | CT.%IB THD | Float | % | 1.0 | . | Actual value | x | Measured value (calculated): IB Total Harmonic Distortion
00001050 | 2 | CT.%IC THD | Float | % | 1.0 | . | Actual value | x | Measured value (calculated): IC Total Harmonic Distortion
00001052 | 2 | ThR.Therm. Lev. | Float | % | 1.0 | . | Actual value | x | Measured value: Ongoing thermal level
00001054 | 2 | Peak Current Ptr.Imax | Float | A | 1.0 | Primary | Actual value | x | Maximum value of the averaged phase current »Iavg« since the last reset
00001056 | 2 | Peak Current Ptr.Iavg | Float | A | 1.0 | Primary | Actual value | x | Maximum value of the phase current, time-averaged over the set time-window As long as the displayed value of »Iavg« is not significant yet, because the calculation is ongoing, the value is displayed as “-0.0”. (After the set time window has elapsed a valid value is displayed.)
00001058 | 2 | Life Load.< 0.4 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001060 | 2 | Life Load.0.4 ... 0.5 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001062 | 2 | Life Load.0.5 ... 0.6 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001064 | 2 | Life Load.0.6 ... 0.7 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001066 | 2 | Life Load.0.7 ... 0.8 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001068 | 2 | Life Load.0.8 ... 0.9 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001070 | 2 | Life Load.0.9 ... 1.0 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001072 | 2 | Life Load.1.0 ... 1.1 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001074 | 2 | Life Load.1.1 ... 1.2 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001076 | 2 | Life Load.> 1.2 In | Float | d | 1.0 | . | Actual value | x | Number of operating days with measured current values within this range
00001078 | 2 | Life Load.Time to Alarm | Float | d | 1.0 | . | Actual value | x | Time (displayed in days) until an alarm signal is issued, because the device has been connected to too high phase currents for a too long time. (The time counts backwards from the »Threshold t« setting to 0. The Direct Command »Rst. Alarm« sets it back to »Threshold t«.)
00001080 | 2 | Sys.Op. Hours | Float | h | 1.0 | . | Actual value | x | Device operation hours counter, that shows for how long the device has been operating since the last restart.
00005000 | 9 | Modbus.Fault rec | Enum (Fault Reasons) | . | . | . | . | x | The communication fault record contains the trip cause and trip time as a structured compound value of words/registers. These are, from low to high address: - [word 0, short] RecordNo - [Word 1, short] Trip Cause - [Word 2, short] Pickup Cause(*) - [Word 3, short] Fault No. - [Word 4, short] No. of Grid Faults - [Word 5 ... Word 8, long long] (WIC returns here only zeros.) (*) Code for the trip cause. In case of several simultaneous trip causes the primary cause is selected. If there is another trip later then the new trip cause overwrites the previous one. The codes for the trip cause are documented in the SCADA documentation.
00010000 | 2 | Sys.Build | Uint32 | . | 1.0 | . | Actual value | x | WIC1: Build Number
00010002 | 8 | Sys.DM version | ASCII String. 16 Bytes | . | . | . | . | x | WIC1: Version of the device model
00010010 | 8 | Sys.SW version | ASCII String. 16 Bytes | . | . | . | . | x | WIC1: Version of the device firmware
00010018 | 8 | Sys.CAT No. | ASCII String. 16 Bytes | . | . | . | . | x | WIC1: »CAT No.«, Order Code as printed on the nameplate of the device.
00010026 | 8 | Sys.REV. | ASCII String. 16 Bytes | . | . | . | . | x | WIC1: Revision (as printed on the nameplate of the device).
00010034 | 8 | Sys.S/N | ASCII String. 16 Bytes | . | . | . | . | x | WIC1: The serial number of the device.
00010100 | 2 | Sys.Build | Uint32 | . | 1.0 | . | Actual value | x | DiggiMEC: Build Number
00010102 | 8 | Sys.DM version | ASCII String. 16 Bytes | . | . | . | . | x | DiggiMEC: Version of the device model
00010110 | 8 | Sys.SW version | ASCII String. 16 Bytes | . | . | . | . | x | DiggiMEC: Version of the device firmware
00010118 | 8 | Sys.CAT No. | ASCII String. 16 Bytes | . | . | . | . | x | DiggiMEC: »CAT No.«, Order Code as printed on the nameplate of the device.
00010126 | 8 | Sys.REV. | ASCII String. 16 Bytes | . | . | . | . | x | DiggiMEC: Revision (as printed on the nameplate of the device).
00010134 | 8 | Sys.S/N | ASCII String. 16 Bytes | . | . | . | . | x | DiggiMEC: The serial number of the device.
00010200 | 2 | TcpIp.Build | Uint32 | . | 1.0 | . | Actual value | x | Build Number
00010202 | 8 | TcpIp.SW version | ASCII String. 16 Bytes | . | . | . | . | x | Version of the device firmware
00010210 | 8 | TcpIp.Interf. Type | ASCII String. 16 Bytes | . | . | . | . | x | Specification of the (built-in) hardware module for the communication interface
00011000 | 2 | CT.IA | Float | A | 1.0 | Primary | Fault value | x | Measured value: Phase current (fundamental)
00011002 | 2 | CT.IB | Float | A | 1.0 | Primary | Fault value | x | Measured value: Phase current (fundamental)
00011004 | 2 | CT.IC | Float | A | 1.0 | Primary | Fault value | x | Measured value: Phase current (fundamental)
00011006 | 2 | CT.IG meas | Float | A | 1.0 | Primary | Fault value | x | Measured value (measured): IG (fundamental)
00011008 | 2 | CT.IG calc | Float | A | 1.0 | Primary | Fault value | x | Measured value (calculated): IG (fundamental) Since the value might be unreliable or invalid for low phase currents it is displayed as “-0.0” in this case.
00011010 | 2 | CT.phi IA | Float | ° | 1.0 | . | Fault value | x | Measured value (calculated): Angle of Phasor IA Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00011012 | 2 | CT.phi IB | Float | ° | 1.0 | . | Fault value | x | Measured value (calculated): Angle of Phasor IB Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00011014 | 2 | CT.phi IC | Float | ° | 1.0 | . | Fault value | x | Measured value (calculated): Angle of Phasor IC Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00011016 | 2 | CT.phi IG meas | Float | ° | 1.0 | . | Fault value | x | Measured value (calculated): Angle of Phasor IG meas Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00011020 | 2 | CT.phi IG calc | Float | ° | 1.0 | . | Fault value | x | Measured value (calculated): Angle of Phasor IG calc Since the angle might be unreliable or invalid for a too low amplitude it is displayed as 360°” in this case.
00011022 | 2 | CT.IA H2 | Float | % | 1.0 | . | Fault value | x | Measured Value: Ratio of 2nd harmonic over fundamental of IA
00011024 | 2 | CT.IB H2 | Float | % | 1.0 | . | Fault value | x | Measured Value: Ratio of 2nd harmonic over fundamental of IB
00011026 | 2 | CT.IC H2 | Float | % | 1.0 | . | Fault value | x | Measured Value: Ratio of 2nd harmonic over fundamental of IC
00011028 | 2 | CT.I0 | Float | A | 1.0 | Primary | Fault value | x | Measured value (calculated): Zero current (fundamental)
00011030 | 2 | CT.I1 | Float | A | 1.0 | Primary | Fault value | x | Measured value (calculated): Positive phase sequence current (fundamental)
00011032 | 2 | CT.I2 | Float | A | 1.0 | Primary | Fault value | x | Measured value (calculated): Unbalanced load current (fundamental)
00011034 | 2 | CT.%(I2/I1) | Float | % | 1.0 | . | Fault value | x | Measured value (calculated): I2/I1, phase sequence will be taken into account automatically.
00011036 | 2 | CT.IA RMS | Float | A | 1.0 | Primary | Fault value | x | Measured value: Phase current (RMS)
00011038 | 2 | CT.IB RMS | Float | A | 1.0 | Primary | Fault value | x | Measured value: Phase current (RMS)
00011040 | 2 | CT.IC RMS | Float | A | 1.0 | Primary | Fault value | x | Measured value: Phase current (RMS)
00011042 | 2 | CT.IG meas RMS | Float | A | 1.0 | Primary | Fault value | x | Measured value (measured): IG (RMS)
00011044 | 2 | CT.IG calc RMS | Float | A | 1.0 | Primary | Fault value | x | Measured value (calculated): IG (RMS) Since the value might be unreliable or invalid for low phase currents it is displayed as “-0.0” in this case.
00011052 | 2 | ThR.Therm. Lev. | Float | % | 1.0 | . | Fault value | x | Measured value: Ongoing thermal level
00030000 | 1 | IH2.Mode | Selection List (Help text) | . | . | . | . | x | Module Inrush, general operation mode 0 = - 1 = use
00030001 | 1 | I>.Mode | Selection List (Help text) | . | . | . | . | x | Phase Overcurrent Stage, general operation mode 0 = - 1 = use
00030002 | 1 | I>>.Mode | Selection List (Help text) | . | . | . | . | x | Phase Overcurrent Stage, general operation mode 0 = - 1 = use
00030003 | 1 | I>>>.Mode | Selection List (Help text) | . | . | . | . | x | Phase Overcurrent Stage, general operation mode 0 = - 1 = use
00030004 | 1 | IG>.Mode | Selection List (Help text) | . | . | . | . | x | Earth current protection stage, general operation mode 0 = - 1 = use
00030005 | 1 | IG>>.Mode | Selection List (Help text) | . | . | . | . | x | Earth current protection stage, general operation mode 0 = - 1 = use
00030006 | 1 | I2/I1>.Mode | Selection List (Help text) | . | . | . | . | x | Unbalanced Load-Stage, general operation mode 0 = - 1 = use 2 = - 3 = use
00030007 | 1 | I2>.Mode | Selection List (Help text) | . | . | . | . | x | Unbalanced Load-Stage, general operation mode 0 = - 1 = use 2 = - 3 = use
00030008 | 1 | ThR.Mode | Selection List (Help text) | . | . | . | . | x | Thermal replica module, general operation mode 0 = - 1 = use
00030009 | 1 | Ipeak>.Mode | Selection List (Help text) | . | . | . | . | x | Peak-Value Overcurrent, general operation mode 0 = - 1 = use
00030010 | 1 | SOTF.Mode | Selection List (Help text) | . | . | . | . | x | Switch Onto Fault - Module, general operation mode 0 = - 1 = use
00030011 | 1 | ExP[1].Mode | Selection List (Help text) | . | . | . | . | x | External Protection - Module, general operation mode 0 = - 1 = use
00030012 | 1 | ExP[2].Mode | Selection List (Help text) | . | . | . | . | x | External Protection - Module, general operation mode 0 = - 1 = use
00030013 | 1 | TCM.Mode | Selection List (Help text) | . | . | . | . | x | Trip Circuit Supervision, general operation mode 0 = - 1 = use
00030014 | 1 | CBF.Mode | Selection List (Help text) | . | . | . | . | x | Module Circuit Breaker Failure protection, general operation mode 0 = - 1 = use
00030015 | 1 | BkrWear.Mode | Selection List (Help text) | . | . | . | . | x | Circuit Breaker Monitoring, general operation mode 0 = - 1 = Counters only 2 = Counters, Wear Lev.
00030016 | 1 | CLPU.Mode | Selection List (Help text) | . | . | . | . | x | Cold Load Pickup Module, general operation mode 0 = - 1 = use
00030017 | 1 | SBM.Mode | Selection List (Help text) | . | . | . | . | x | Station Battery Monitoring, general operation mode 0 = - 1 = use
00030018 | 1 | Life Load.Mode | Selection List (Help text) | . | . | . | . | x | Load Current Histogram, general operation mode 0 = - 1 = use
00030019 | 1 | Modbus.Mode | Selection List (Help text) | . | . | . | . | x | Modbus Protocol, general operation mode 0 = - 1 = RTU 2 = - 3 = TCP
00030020 | 1 | Sgen.Mode | Selection List (Help text) | . | . | . | . | x | Sine wave generator, general operation mode 0 = - 1 = use
00030021 | 1 | Prot.Meth.Detect.Bkr.Pos. | Selection List (Help text) | . | . | . | . | x | Select the method to be used to determine the connected breaker position. 0 = Current-Based 1 = Aux-Based 2 = Current and Aux
00030022 | 2 | Prot.I ON | Float | A | . | . | . | x | The breaker is determined as ON (closed) based on current measurement if any phase current is greater than this value (for at least the settable duration »t ON/OFF«).
00030024 | 1 | Prot.Aux ON | Selection List (Help text) | . | . | . | . | x | The CB is in ON-position if the state of the assigned signal is true (52a). 0 = - 1 = DI 1 2 = DI 2 3 = -
00030025 | 1 | Prot.Aux OFF | Selection List (Help text) | . | . | . | . | x | The CB is in OFF-position if the state of the assigned signal is true (52b). 0 = - 1 = DI 1 2 = DI 2 3 = -
00030026 | 1 | Prot.SCmd ON | Selection List (Help text) | . | . | . | . | x | Switching ON Command, e.g. the state of the digital input 0 = - 1 = DI 1 2 = DI 2 3 = -
00030027 | 1 | Prot.ExBlo TripCmd | Selection List (Help text) | . | . | . | . | x | If external blocking of the tripping command is activated (allowed), the tripping command of the entire device will be blocked if the state of the assigned signal becomes true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030028 | 1 | IH2.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030029 | 2 | IH2.IH2 / IH1 | Float | % | . | . | . | x | Maximum permissible percentage of the 2nd harmonic of the 1st harmonic.
00030031 | 2 | IH2.Imax | Float | A | . | . | . | x | Inrush limit value: If the phase current is above this value the inrush blocking is cancelled.
00030033 | 2 | IH2.tmax | Float | s | . | . | . | x | Maximum duration (phase-selective) of an inrush blocking
00030035 | 1 | IH2.3-ph Blo | Selection List (Help text) | . | . | . | . | x | Activation of 3-phase inrush blocking: If an inrush is detected in (at least) one phase all three phases get blocked. (If this is inactive then only the Inrush-affected phase gets blocked.) 0 = Inactive 1 = Active
00030036 | 1 | I>.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030037 | 2 | I>.I | Float | A | . | . | . | x | If the pickup value is exceeded, the protection stage starts to time out to trip. WARNING: Check the Technical Data and ensure that the actual overcurrent settings for this pickup threshold and the trip delay comply with the technical limits of the phase current inputs! (The device allows for overcurrent settings that are out of the permitted range of current values.)
00030039 | 1 | I>.Char | Selection List (Help text) | . | . | . | . | x | Characteristic 0 = DEFT 1 = IEC NINV 2 = IEC VINV 3 = IEC EINV 4 = IEC LINV 5 = RINV 6 = HV Fuse 7 = FR Fuse 8 = IEEE MINV 9 = IEEE VINV 10 = IEEE EINV 11 = EF Curve
00030040 | 2 | I>.t | Float | s | . | . | . | x | Time delay for trip or alarm
00030042 | 2 | I>.tChar | Float | . | . | . | . | x | Time multiplier/tripping characteristic factor. The setting range depends on the selected tripping curve.
00030044 | 2 | I>.tMinimum | Float | s | . | . | . | x | Minimum trip delay time. Independent of the measured current values, the trip delay time does never fall below the minimum that is set here.
00030046 | 1 | I>.Reset Mode | Selection List (Help text) | . | . | . | . | x | Reset Mode 0 = instantaneous 1 = definite time 2 = inverse time
00030047 | 2 | I>.tReset | Float | s | . | . | . | x | Reset delay for intermittent phase failures (INV characteristics only)
00030049 | 1 | I>.IH2 Blo | Selection List (Help text) | . | . | . | . | x | Blocking the trip command, if an inrush is detected. 0 = Inactive 1 = Active
00030050 | 1 | I>.Stab. by CLPU | Selection List (Help text) | . | . | . | . | x | Select whether the CLPU stabilization shall be effective for this protection stage. (If set to “active” then further settings are available within the CLPU menu.) 0 = Inactive 1 = Active
00030051 | 1 | I>.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030052 | 1 | I>>.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030053 | 2 | I>>.I | Float | A | . | . | . | x | If the pickup value is exceeded, the protection stage starts to time out to trip. WARNING: Check the Technical Data and ensure that the actual overcurrent settings for this pickup threshold and the trip delay comply with the technical limits of the phase current inputs! (The device allows for overcurrent settings that are out of the permitted range of current values.)
00030055 | 1 | I>>.Char | Selection List (Help text) | . | . | . | . | x | Characteristic 0 = DEFT 1 = IEC NINV 2 = IEC VINV 3 = IEC EINV 4 = IEC LINV 5 = RINV 6 = HV Fuse 7 = FR Fuse 8 = IEEE MINV 9 = IEEE VINV 10 = IEEE EINV 11 = EF Curve
00030056 | 2 | I>>.t | Float | s | . | . | . | x | Time delay for trip or alarm
00030058 | 2 | I>>.tChar | Float | . | . | . | . | x | Time multiplier/tripping characteristic factor. The setting range depends on the selected tripping curve.
00030060 | 2 | I>>.tMinimum | Float | s | . | . | . | x | Minimum trip delay time. Independent of the measured current values, the trip delay time does never fall below the minimum that is set here.
00030062 | 1 | I>>.Reset Mode | Selection List (Help text) | . | . | . | . | x | Reset Mode 0 = instantaneous 1 = definite time 2 = inverse time
00030063 | 2 | I>>.tReset | Float | s | . | . | . | x | Reset delay for intermittent phase failures (INV characteristics only)
00030065 | 1 | I>>.IH2 Blo | Selection List (Help text) | . | . | . | . | x | Blocking the trip command, if an inrush is detected. 0 = Inactive 1 = Active
00030066 | 1 | I>>.Stab. by CLPU | Selection List (Help text) | . | . | . | . | x | Select whether the CLPU stabilization shall be effective for this protection stage. (If set to “active” then further settings are available within the CLPU menu.) 0 = Inactive 1 = Active
00030067 | 1 | I>>.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030068 | 1 | I>>>.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030069 | 2 | I>>>.I | Float | A | . | . | . | x | If the pickup value is exceeded, the protection stage starts to time out to trip. WARNING: Check the Technical Data and ensure that the actual overcurrent settings for this pickup threshold and the trip delay comply with the technical limits of the phase current inputs! (The device allows for overcurrent settings that are out of the permitted range of current values.)
00030071 | 1 | I>>>.Char | Selection List (Help text) | . | . | . | . | x | Characteristic 0 = DEFT 1 = IEC NINV 2 = IEC VINV 3 = IEC EINV 4 = IEC LINV 5 = RINV 6 = HV Fuse 7 = FR Fuse 8 = IEEE MINV 9 = IEEE VINV 10 = IEEE EINV 11 = EF Curve
00030072 | 2 | I>>>.t | Float | s | . | . | . | x | Time delay for trip or alarm
00030074 | 2 | I>>>.tChar | Float | . | . | . | . | x | Time multiplier/tripping characteristic factor. The setting range depends on the selected tripping curve.
00030076 | 2 | I>>>.tMinimum | Float | s | . | . | . | x | Minimum trip delay time. Independent of the measured current values, the trip delay time does never fall below the minimum that is set here.
00030078 | 1 | I>>>.Reset Mode | Selection List (Help text) | . | . | . | . | x | Reset Mode 0 = instantaneous 1 = definite time 2 = inverse time
00030079 | 2 | I>>>.tReset | Float | s | . | . | . | x | Reset delay for intermittent phase failures (INV characteristics only)
00030081 | 1 | I>>>.IH2 Blo | Selection List (Help text) | . | . | . | . | x | Blocking the trip command, if an inrush is detected. 0 = Inactive 1 = Active
00030082 | 1 | I>>>.Stab. by CLPU | Selection List (Help text) | . | . | . | . | x | Select whether the CLPU stabilization shall be effective for this protection stage. (If set to “active” then further settings are available within the CLPU menu.) 0 = Inactive 1 = Active
00030083 | 1 | I>>>.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030084 | 1 | IG>.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030085 | 2 | IG>.IG | Float | A | . | . | . | x | If the pickup value is exceeded, the protection stage starts to time out to trip.
00030087 | 1 | IG>.Char | Selection List (Help text) | . | . | . | . | x | Characteristic 0 = DEFT 1 = IEC NINV 2 = IEC VINV 3 = IEC EINV 4 = IEC LINV 5 = RINV 6 = HV Fuse 7 = FR Fuse 8 = IEEE MINV 9 = IEEE VINV 10 = IEEE EINV 11 = EF Curve 12 = RXIDG
00030088 | 2 | IG>.t | Float | s | . | . | . | x | Time delay for trip or alarm
00030090 | 2 | IG>.tChar | Float | . | . | . | . | x | Time multiplier/tripping characteristic factor. The setting range depends on the selected tripping curve.
00030092 | 2 | IG>.tMinimum | Float | s | . | . | . | x | Minimum trip delay time. Independent of the measured current values, the trip delay time does never fall below the minimum that is set here.
00030094 | 1 | IG>.Reset Mode | Selection List (Help text) | . | . | . | . | x | Reset Mode 0 = instantaneous 1 = definite time 2 = inverse time
00030095 | 2 | IG>.tReset | Float | s | . | . | . | x | Reset delay for intermittent phase failures (INV characteristics only)
00030097 | 1 | IG>.IH2 Blo | Selection List (Help text) | . | . | . | . | x | Blocking the trip command, if an inrush is detected. 0 = Inactive 1 = Active
00030098 | 1 | IG>.Stab. by CLPU | Selection List (Help text) | . | . | . | . | x | Select whether the CLPU stabilization shall be effective for this protection stage. (If set to “active” then further settings are available within the CLPU menu.) 0 = Inactive 1 = Active
00030099 | 1 | IG>.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030100 | 1 | IG>>.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030101 | 2 | IG>>.IG | Float | A | . | . | . | x | If the pickup value is exceeded, the protection stage starts to time out to trip.
00030103 | 1 | IG>>.Char | Selection List (Help text) | . | . | . | . | x | Characteristic 0 = DEFT 1 = IEC NINV 2 = IEC VINV 3 = IEC EINV 4 = IEC LINV 5 = RINV 6 = HV Fuse 7 = FR Fuse 8 = IEEE MINV 9 = IEEE VINV 10 = IEEE EINV 11 = EF Curve 12 = RXIDG
00030104 | 2 | IG>>.t | Float | s | . | . | . | x | Time delay for trip or alarm
00030106 | 2 | IG>>.tChar | Float | . | . | . | . | x | Time multiplier/tripping characteristic factor. The setting range depends on the selected tripping curve.
00030108 | 2 | IG>>.tMinimum | Float | s | . | . | . | x | Minimum trip delay time. Independent of the measured current values, the trip delay time does never fall below the minimum that is set here.
00030110 | 1 | IG>>.Reset Mode | Selection List (Help text) | . | . | . | . | x | Reset Mode 0 = instantaneous 1 = definite time 2 = inverse time
00030111 | 2 | IG>>.tReset | Float | s | . | . | . | x | Reset delay for intermittent phase failures (INV characteristics only)
00030113 | 1 | IG>>.IH2 Blo | Selection List (Help text) | . | . | . | . | x | Blocking the trip command, if an inrush is detected. 0 = Inactive 1 = Active
00030114 | 1 | IG>>.Stab. by CLPU | Selection List (Help text) | . | . | . | . | x | Select whether the CLPU stabilization shall be effective for this protection stage. (If set to “active” then further settings are available within the CLPU menu.) 0 = Inactive 1 = Active
00030115 | 1 | IG>>.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030116 | 1 | I2/I1>.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030117 | 2 | I2/I1>.I2/I1 | Float | % | . | . | . | x | I2/I1 unbalance trip pickup setting (in percent), i.e. the ratio of negative sequence current I2 to the positive sequence current I1.
00030119 | 2 | I2/I1>.t | Float | s | . | . | . | x | Time delay for trip or alarm
00030121 | 1 | I2/I1>.IH2 Blo | Selection List (Help text) | . | . | . | . | x | Blocking the trip command, if an inrush is detected. 0 = Inactive 1 = Active
00030122 | 1 | I2/I1>.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030123 | 1 | I2>.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030124 | 2 | I2>.I2 | Float | A | . | . | . | x | The Threshold setting defines a minimum operating current magnitude of I2 for the 46 function to operate, which ensures that the relay has a solid basis for initiating a current unbalance trip. This is a supervisory function and not a trip level.
00030126 | 1 | I2>.Char | Selection List (Help text) | . | . | . | . | x | Characteristic 0 = DEFT 1 = IEC NINV 2 = IEC VINV 3 = IEC EINV 4 = IEC LINV 5 = RINV 6 = HV Fuse 7 = FR Fuse 8 = IEEE MINV 9 = IEEE VINV 10 = IEEE EINV 11 = EF Curve
00030127 | 2 | I2>.t | Float | s | . | . | . | x | Time delay for trip or alarm
00030129 | 2 | I2>.tChar | Float | . | . | . | . | x | Time multiplier/tripping characteristic factor. The setting range depends on the selected tripping curve.
00030131 | 2 | I2>.tMinimum | Float | s | . | . | . | x | Minimum trip delay time. Independent of the measured current values, the trip delay time does never fall below the minimum that is set here.
00030133 | 1 | I2>.Reset Mode | Selection List (Help text) | . | . | . | . | x | Reset Mode 0 = instantaneous 1 = definite time 2 = inverse time
00030134 | 2 | I2>.tReset | Float | s | . | . | . | x | Reset delay for intermittent phase failures (INV characteristics only)
00030136 | 1 | I2>.IH2 Blo | Selection List (Help text) | . | . | . | . | x | Blocking the trip command, if an inrush is detected. 0 = Inactive 1 = Active
00030137 | 1 | I2>.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030138 | 1 | ThR.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030139 | 2 | ThR.Ib | Float | A | . | . | . | x | Base current: Maximum permissible thermal continuous current.
00030141 | 2 | ThR.K | Float | . | . | . | . | x | Overload Factor: The maximum thermal limit is defined as k*IB, the product of the overload factor and the base current.
00030143 | 2 | ThR.Pre-Alarm Lev. | Float | % | . | . | . | x | Threshold value for the Thermal Level. If the thermal level exceeds this setting the signal »ThR . Pre-Alarm« is issued.
00030145 | 2 | ThR.τ-warm | Float | s | . | . | . | x | Warming-up time constant
00030147 | 2 | ThR.τ-cool | Float | s | . | . | . | x | Cooling time constant
00030149 | 1 | ThR.Initial Thermal Level | Selection List (Help text) | . | . | . | . | x | Select the criterion for setting the initial thermal level after a restart of the device. 0 = Zero 1 = Last Stored Value
00030150 | 1 | ThR.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030151 | 1 | Ipeak>.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030152 | 2 | Ipeak>.I | Float | A | . | . | . | x | Pickup threshold, defined as RMS value (i.e. peak current value divided by √2). If the pickup value is exceeded, the module/element starts to time out to trip.
00030154 | 2 | Ipeak>.t | Float | s | . | . | . | x | Time delay for trip or alarm
00030156 | 1 | Ipeak>.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030157 | 1 | SOTF.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030158 | 1 | SOTF.Enabling | Selection List (Help text) | . | . | . | . | x | Select the criterion for determining a manual CLOSE of the breaker. (After this, the »SOTF« module gets enabled for a particular settable time.) 0 = Breaker Pos. 1 = Close Command
00030159 | 2 | SOTF.t-enable | Float | s | . | . | . | x | While this timer is running, and while the module is not blocked, the Switch Onto Fault Module is effective (SOTF is armed).
00030161 | 2 | SOTF.t | Float | s | . | . | . | x | Time delay for trip or alarm. (For the »SOTF« module, an instantaneous tripping is typical, i.e. the setting value 0 s.)
00030163 | 1 | SOTF.Trigger | Selection List (Help text) | . | . | . | . | x | Assign the type of pickup signal that triggers the SOTF module. If the assigned pickup signal is issued, the SOTF module itself picks up. 0 = -.- 1 = I>.Pickup 2 = I>>.Pickup 3 = I>>>.Pickup 4 = Ipeak>.Pickup 5 = Prot.Pickup
00030164 | 1 | SOTF.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030165 | 1 | ExP[1].Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030166 | 2 | ExP[1].t | Float | s | . | . | . | x | Time delay for trip or alarm
00030168 | 1 | ExP[1].Trigger Signal | Selection List (Help text) | . | . | . | . | x | Assign the trigger signal that will make the »ExP« module start (pickup). 0 = - 1 = DI 1 2 = DI 2 3 = -
00030169 | 1 | ExP[1].ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030170 | 1 | ExP[2].Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030171 | 2 | ExP[2].t | Float | s | . | . | . | x | Time delay for trip or alarm
00030173 | 1 | ExP[2].Trigger Signal | Selection List (Help text) | . | . | . | . | x | Assign the trigger signal that will make the »ExP« module start (pickup). 0 = - 1 = DI 1 2 = DI 2 3 = -
00030174 | 1 | ExP[2].Condition | Selection List (Help text) | . | . | . | . | x | Assign a signal that must be active in additon to the external signal for making the »ExP« module start (pickup). (If no signal has been assigned here then the »ExP« module always picks up as soon as the external signal becomes active.) 0 = -.- 1 = I>.Pickup 2 = I>>.Pickup 3 = I>>>.Pickup 4 = Ipeak>.Pickup 5 = Prot.Pickup
00030175 | 1 | ExP[2].ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030176 | 1 | TCM.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030177 | 1 | TCM.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030178 | 1 | CBF.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030179 | 2 | CBF.t-CBF | Float | s | . | . | . | x | If the delay time is expired, a CBF alarm is issued.
00030181 | 1 | CBF.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030182 | 1 | CLPU.Function | Selection List (Help text) | . | . | . | . | x | Permanent activation or deactivation of module/stage. 0 = Inactive 1 = Active
00030183 | 1 | CLPU.50/51 Stab. | Selection List (Help text) | . | . | . | . | x | Select whether the CLPU stabilization shall be effective for the Phase Overcurrent stages, and which operating mode shall be used. 0 = inactive 1 = Factor 2 = Block.
00030184 | 2 | CLPU.50, 51 Factor | Float | % | . | . | . | x | If the operating mode has been set to increase the pickup threshold then this is the factor by which the pickup threshold of each the Phase Overcurrent stage is multiplied during the CLPU stabilization.
00030186 | 1 | CLPU.50 N/G, 51 N/G Stab. | Selection List (Help text) | . | . | . | . | x | Select whether the CLPU stabilization shall be effective for the Ground (Earth) Overcurrent stages, and which operating mode shall be used. 0 = inactive 1 = Factor 2 = Block.
00030187 | 2 | CLPU.50 N/G, 51 N/G Factor | Float | % | . | . | . | x | If the operating mode has been set to increase the pickup threshold then this is the factor by which the pickup threshold of each the Ground (Earth) Overcurrent stage is multiplied during the CLPU stabilization.
00030189 | 2 | CLPU.tOff | Float | min | . | . | . | x | Timer stage, that is started when the breaker position is detected as Off. (The next re-energization after this timer has expired will trigger the CLPU stabilization.)
00030191 | 2 | CLPU.tStab | Float | s | . | . | . | x | Duration of the CLPU stabilization. This timer stage is started when the CLPU stabilization is triggered.
00030193 | 1 | CLPU.ExBlo | Selection List (Help text) | . | . | . | . | x | External blocking of the module if the state of the assigned signal is true. Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030194 | 1 | CT.Phase Sequence | Selection List (Help text) | . | . | . | . | x | Phase Sequence 0 = ABC 1 = ACB
00030195 | 1 | CT.f | Selection List (Help text) | . | . | . | . | x | Nominal frequency 0 = 50 1 = 60
00030196 | 1 | CT.Measuring method | Selection List (Help text) | . | . | . | . | x | Measuring method for the protection stages I>, I>>, I>>>, IG>, IG>>: Fundamental or RMS 0 = Fundamental 1 = True RMS
00030197 | 1 | CT.IG Source | Selection List (Help text) | . | . | . | . | x | Selection if measured or calculated ground current should be used. 0 = calculated 1 = measured
00030198 | 1 | CT.Display of Meas. Values | Selection List (Help text) | . | . | . | . | x | Select the preferred scaling/unit for the display of measurement values. 0 = Based on In,relative 1 = Primary current values 2 = Secondary current val.
00030199 | 1 | CT.CT Type | Selection List (Help text) | . | . | . | . | x | Select the connected CT Type 0 = Relative 1 = WE2 : 16 A ... 56 A 2 = W2 : 16 A ... 56 A 3 = W3 : 32 A ... 112 A 4 = W4 : 64 A ... 224 A 5 = W5 : 128 A ... 448 A 6 = W6 : 256 A ... 896 A 7 = WC1 8 = WC2
00030200 | 2 | CT.In,relative | Float | In.min | . | . | . | x | Relative primary rated current. (This is the rated current divided by the CT ratio, i.e. a value that has been made independent of the CT type.)
00030202 | 2 | CT.CT pri | Float | A | . | . | . | x | Nominal current of the primary side of the current transformers.
00030204 | 2 | CT.ECT pri | Float | A | . | . | . | x | This parameter defines the primary nominal current of the connected earth current transformer. If the earth current is measured via the Holmgreen connection, the primary value of the phase current transformer must be entered here.
00030206 | 1 | CT.CT Shift by 0°/180° | Selection List (Help text) | . | . | . | . | x | If this is set to 180° the phase current vectors are shifted by 180 degrees (change of sign), by device-internal calculation, i.e. without modification of the wiring. 0 = 0 1 = 180
00030207 | 1 | CT.ECT Shift by 0°/180° | Selection List (Help text) | . | . | . | . | x | If this is set to 180° the ground current vector is shifted by 180 degrees (change of sign), by device-internal calculation, i.e. without modification of the wiring. 0 = 0 1 = 180
00030208 | 1 | Prot.Nom voltage | Selection List (Help text) | . | . | . | . | x | Nominal voltage of the digital inputs 0 = 24 VDC 1 = 48 VDC ... 60 VDC 2 = 110 VDC 3 = 230 VDC 4 = 110 VAC 5 = 230 VAC 6 = 115 VAC / 230 VAC
00030209 | 1 | Prot.Out. Mode | Selection List (Help text) | . | . | . | . | x | Select whether the output shall operate as an impulse output (for connecting a flag indicator with full compatibility to the 1st generation WIC1), or as a relay output (with a fixed, pre-defined usage as a self-supervision contact). (The usage as a self-supervision contact is only possible with an externally supplied WIC1-4, and connecting a flag indicator is not permissible with this setting.) 0 = Impulse Output 1 = Syst. O.K. & Ext.Suppl. 2 = Relay Output
00030210 | 1 | Prot.Out. assign. | Selection List (Help text) | . | . | . | . | x | Assign the signal that shall activate the output. (If the output is set as impulse output the signal triggers the impulses for the connected Flag Indicator. If it is set as relay output the signal sets it to the “active” state.) Selection list value description is in register sheet 'Enum (List of Ext.Blockade)'.
00030211 | 1 | Prot.Out. Inverting | Selection List (Help text) | . | . | . | . | x | Inverting of the signal that has been assigned to the output. 0 = Inactive 1 = Active
00030212 | 1 | Prot.TCM | Selection List (Help text) | . | . | . | . | x | Trip Circuit Monitoring alam can be linked additionally to FI-Output (only possible with Device option with Selfsupervision) 0 = Inactive 1 = Active
00030213 | 1 | Prot.Assign Ext. Reset | Selection List (Help text) | . | . | . | . | x | Assign an digital input signal that, when it becomes true, will reset all latched LEDs, all DiggiMEC Flag Indicators, and a fault/trip info that might be visible on the DiggiMEC display. 0 = - 1 = DI 1 2 = DI 2 3 = -
00030214 | 1 | Prot.Def. Autom. Reset | Selection List (Help text) | . | . | . | . | x | The automatic reset will reset all latched LEDs, all DiggiMEC Flag Indicators, and a fault/trip info that might be visible on the DiggiMEC display. This is done depending on this setting, when a new protection pickup occurs or after a particular time has elapsed. 0 = OFF (No Autom. Reset) 1 = With a New Pickup 2 = New Pickup or After 1 h 3 = New Pickup or After 2 h 4 = New Pickup or After 4 h 5 = New Pickup or After 8 h 6 = New Pickup or After 12 h 7 = New Pickup or After 24 h 8 = New Pickup or After 10 s
00030215 | 1 | I>.Definition | Selection List (Help text) | . | . | . | . | x | Phase Overcurrent Stage: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030216 | 1 | I>>.Definition | Selection List (Help text) | . | . | . | . | x | Phase Overcurrent Stage: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030217 | 1 | I>>>.Definition | Selection List (Help text) | . | . | . | . | x | Phase Overcurrent Stage: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030218 | 1 | IG>.Definition | Selection List (Help text) | . | . | . | . | x | Earth current protection stage: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030219 | 1 | IG>>.Definition | Selection List (Help text) | . | . | . | . | x | Earth current protection stage: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030220 | 1 | I2/I1>.Definition | Selection List (Help text) | . | . | . | . | x | Unbalanced Load-Stage: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030221 | 1 | I2>.Definition | Selection List (Help text) | . | . | . | . | x | Unbalanced Load-Stage: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030222 | 1 | ThR.Definition | Selection List (Help text) | . | . | . | . | x | Thermal replica module: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030223 | 1 | Ipeak>.Definition | Selection List (Help text) | . | . | . | . | x | Peak-Value Overcurrent: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030224 | 1 | SOTF.Definition | Selection List (Help text) | . | . | . | . | x | Switch Onto Fault - Module: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030225 | 1 | ExP[1].Definition | Selection List (Help text) | . | . | . | . | x | External Protection - Module: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
00030226 | 1 | ExP[2].Definition | Selection List (Help text) | . | . | . | . | x | External Protection - Module: If set to “Alarm”: The function operates as a supervision function, i.e. a fault generates neither alarm nor trip, but an »Alarm« signal gets issued instead. If set to “Trip”: The function operates as a protection function, i.e. trips the breaker in case of a fault. 0 = Trip 1 = Alarm
Note for primary: For reading primary value, the current transformer should be defined in the device via [File Para / CT] CT.CT pri. Otherwise responses on these value requests will be zero.

## FC5 (Single Commands)
Address | Information Object | Description
00002000 | Modbus.Scada | Direct Command to reset all Modbus-latched states.(Latched in Map).
00002001 | Modbus.Rst. Counters | Direct Command to reset all Modbus Diagnosis Counters
00002002 | Prot.Rst. LEDs, FIs | Direct Command to immediately reset all latched LEDs, all DiggiMEC Flag Indicators, and the Fault Info Screen that might be visible on the DiggiMEC display.
00002003 | Prot.Rst. Alm/Flt Rec. | Direct Command to immediately delete all entries from the Alarm/Fault Recorder.
00002004 | ThR.Rst. Thermal Lev. | Reset the thermal level
00002005 | Sys.Rst. Err. LED | Direct Command to acknowledge a (device-internal) error. This also resets the System (Ready/Error) LED.
00002006 | BkrWear.Reset | Direct Command to reset the counters and the wear level of the circuit breaker.
00002007 | Peak Current Ptr.Clear | Direct Command to reset the drag indicator for »Imax«
00002008 | Life Load.Rst. Alarm | Direct Command to reset the Alarm signal. This also resets the countdown timer »Time to Alarm« back to the setting value »Threshold t«.

## Enum (Fault Reasons)
Value | Module | Description
1 | Prot | Module General Protection
2 | CT | Current Transformer
5 | DiggiMEC | DiggiMEC
6 | Sys | System
7 | Sgen | Sine wave generator
8 | TcpIp | TcpIp
10 | IH2 | Module Inrush
11 | I> | Phase Overcurrent Stage
12 | I>> | Phase Overcurrent Stage
13 | I>>> | Phase Overcurrent Stage
14 | IG> | Ground (earth) current protection stage
15 | IG>> | Ground (earth) current protection stage
16 | Ipeak> | Peak-Value Overcurrent
17 | I2/I1> | Unbalanced Load Protection
18 | I2> | Negative-Sequence Current Protection
19 | ThR | Thermal replica module
20 | SOTF | Switch Onto Fault - Module
21 | CLPU | Cold Load Pickup Module
22 | ExP[1] | External Protection - Module
23 | ExP[2] | External Protection - Module
30 | TCM | Trip Circuit Monitoring
31 | CBF | Circuit breaker failure protection module
32 | BkrWear | Breaker Wear
33 | SBM | Station Battery Monitoring
58 | Life Load | Load Current Histogram
59 | Peak Current Ptr | Statistic of the current measuring values
60 | Modbus | Modbus
Note: Not all modules cause fault recorder records to be stored.

## Enum (Ext. Blocking)
Value | Name | Description
0 | -.-
1 | IH2.Block. A | Signal: Inrush blocking of phase A of the phase overcurrent protection
2 | IH2.Block. B | Signal: Inrush blocking of phase B of the phase overcurrent protection
3 | IH2.Block. C | Signal: Inrush blocking of phase C of the phase overcurrent protection
4 | IH2.Block. Ground | Signal: Inrush blocking of the ground (earth) overcurrent protection and min. 1 phase of the phase overcurrent protection.
5 | IH2.Block. 3-ph | Signal: 3-phase Inrush blocking: An inrush has been detected in (at least) one phase, so that all three phases are blocked.
6 | I>.Trip | Signal: Trip
7 | I>.Alarm | Signal: Alarm
8 | I>.Pickup | Signal: Pickup
9 | I>>.Trip | Signal: Trip
10 | I>>.Alarm | Signal: Alarm
11 | I>>.Pickup | Signal: Pickup
12 | I>>>.Trip | Signal: Trip
13 | I>>>.Alarm | Signal: Alarm
14 | I>>>.Pickup | Signal: Pickup
15 | IG>.Trip | Signal: Trip
16 | IG>.Alarm | Signal: Alarm
17 | IG>.Pickup | Signal: Pickup
18 | IG>.IH2 Blo | Signal: Blocking the trip command by an inrush
19 | IG>>.Trip | Signal: Trip
20 | IG>>.Alarm | Signal: Alarm
21 | IG>>.Pickup | Signal: Pickup
22 | IG>>.IH2 Blo | Signal: Blocking the trip command by an inrush
23 | I2/I1>.Trip | Signal: Trip
24 | I2/I1>.Alarm | Signal: Alarm
25 | I2/I1>.Pickup | Signal: Pickup
26 | I2/I1>.IH2 Blo | Signal: Blocking the trip command by an inrush
27 | I2>.Trip | Signal: Trip
28 | I2>.Alarm | Signal: Alarm
29 | I2>.Pickup | Signal: Pickup
30 | I2>.IH2 Blo | Signal: Blocking the trip command by an inrush
31 | ThR.Trip | Signal: Trip
32 | ThR.Alarm | Signal: Alarm
33 | ThR.Pickup | Signal: Pickup
34 | ThR.Pre-Alarm | Signal: The set value for the Θ Threshold has been exceeded.
35 | Ipeak>.Trip | Signal: Trip
36 | Ipeak>.Alarm | Signal: Alarm
37 | Ipeak>.Pickup | Signal: Pickup
38 | SOTF.Trip | Signal: Trip
39 | SOTF.Alarm | Signal: Alarm
40 | SOTF.Pickup | Signal: Pickup
41 | ExP[1].Trip | Signal: Trip
42 | ExP[1].Alarm | Alarm
43 | ExP[1].Pickup | Signal: Pickup
44 | ExP[2].Trip | Signal: Trip
45 | ExP[2].Alarm | Alarm
46 | ExP[2].Pickup | Signal: Pickup
47 | TCM.Alarm | Signal: Alarm
48 | CBF.Alarm | Signal: Alarm
49 | BkrWear.Alarm | Signal: Alarm: The maximum number of open commands or the maximum value for the sum of ruptured currents has been exceeded.
50 | BkrWear.Alm(mx.Sum.Tr) | Signal: Alarm: The maximum number of open commands has been exceeded.
51 | BkrWear.Alm(mx.Sum.Itrip) | Signal: Alarm: The maximum value for the sum of ruptured currents has been exceeded.
52 | BkrWear.Alm (CB Wear Lev.) | Signal: Alarm: The maximum wear level of the circuit breaker has been exceeded.
53 | CLPU.detected | Signal: The CLPU stabilization has been triggered.
54 | CLPU.stab. | Signal: The CLPU stabilization is active.
55 | SBM.Trip | Signal: Trip
56 | SBM.Alarm | Signal: Alarm
57 | SBM.Pickup | Signal: Pickup
58 | SBM.Trip VBatt<< | Signal: Trip because the station battery voltage has dropped below VBatt<<
59 | SBM.Alarm VBatt> | Signal: Alarm because the station battery voltage has exceeded VBatt>
60 | SBM.Alarm VBatt< | Signal: Alarm because the station battery voltage has dropped below VBatt<
61 | SBM.Alarm VBatt<< | Signal: Alarm because the station battery voltage has dropped below VBatt<<
62 | SBM.Pickup VBatt> | Signal: Pickup because the station battery voltage has exceeded VBatt>
63 | SBM.Pickup VBatt< | Signal: Pickup because the station battery voltage has dropped below VBatt<
64 | SBM.Pickup VBatt<< | Signal: Pickup because the station battery voltage has dropped below VBatt<<
65 | Life Load.Alarm | Signal: Alarm
66 | Sys.New error/warning | Signal: A new Self-Supervision message (error or warning) has been issued.
67 | Sys.Prot. Ready | Signal: The device has completely booted, all protection functions are running and there is enough electrical energy for a trip pulse.
68 | Sys.Intern.Volt. not OK | Signal: The self-supervision of the device has determined a problem with the internal voltage level or energy supply. This might impair the overall protection functionality, including the possibility to output a trip pulse. (If the supply via the connected CTs is sufficient you might want to check for a potential energy drain through the devices connected to the output(s).)
69 | Sgen.Started | Fault Simulation has been started
70 | Sgen.Running | Signal: Measuring value simulation is running
71 | Sgen.Stopped | Fault Simulation has been stopped
72 | Sgen.Not Running | Signal: Measuring value simulation is not running
73 | Prot.TripCmd | Signal: Trip Command
74 | Prot.Trip | Signal: General Trip
75 | Prot.Alarm | Signal: General Alarm
76 | Prot.Pickup | Signal: General Pickup
77 | Prot.Trip IPh | Signal: General Trip due to a phase current fault
78 | Prot.Trip IG | Signal: General Trip due to a ground current fault
79 | Prot.Trip Ext. | Signal: General Trip due to an external signal
80 | Prot.Trip IA | Signal: General Trip due to a fault in phase A
81 | Prot.Trip IB | Signal: General Trip due to a fault in phase B
82 | Prot.Trip IC | Signal: General Trip due to a fault in phase C
83 | Prot.Pickup I Ph | Signal: General Pickup due to a phase current fault
84 | Prot.Pickup IG | Signal: General Pickup due to a ground current fault
85 | Prot.Pickup Ext. | Signal: General Pickup due to an external signal
86 | Prot.DI 1 | Signal: Digital Input
87 | Prot.DI 2 | Signal: Digital Input
88 | Prot.Pos ON | Signal: Circuit Breaker is in ON-Position
89 | Prot.Pos OFF | Signal: Circuit Breaker is in OFF-Position
90 | Prot.- | none
91 | Prot.- | none